## Legend
Sheet | Indicators | [5 empty] | Weighted factors
| Shortcut | Full name | Indicator | Unit | Scenarios for which this indicator is/will be availabe in TYNDP2022 | Is the indicator available for EU area | 3 Climate years
| ΔSEW | Annual Socio-Economic Welfare (SEW) increase(excluding ENS cost) | B1 | M€ / year | NT2030, DE2030, DE2040 | Yes | 1995 | 0.23
| ΔSEW_CO2 | Annual Socio-Economic Welfare variation resulting from CO2 emmisions | B1_CO2 | M€ / year | NT2030, DE2030, DE2040 | Yes | 2008 | 0.37
| ΔSEW_RES | Annual Socio-Economic Welfare increase resulting from RES integration | B1_RES | M€ / year | NT2030, DE2030, DE2040 | Yes | 2009 | 0.4
Scenario | ΔCO2_market | Annual CO2 varation from market simulation | B2a | ktonnes / year | NT2030, DE2030, DE2040 | Yes
Tool | ΔCO2_network | Annual CO2 varation due to network losses | B2b | ktonnes / year | NT2030, DE2030 | Yes
| ΔCO2_market_SEW | Annual Societal cost variation resulting from CO2 variation from market simulation | B2a_SEW | M€ / year | NT2030, DE2030, DE2040 | Yes
| ΔCO2_network_SEW | Annual Societal cost variation resulting from CO2 variation from network simulation | B2b_SEW | M€ / year | NT2030, DE2030 | Yes
| ΔRES | Annual avoided curtailment (RES integration) | B3 | GWh / year | NT2030, DE2030, DE2040 | Yes
| ΔRES_MW | Connected RES | B3a | MW | NT2030, DE2030, DE2040 | Yes
| ΔNOx | Nitrogen oxides | B4a | kg / year | NT2030, DE2030 | Yes
| ΔNH3 | Ammonia | B4b | kg / year | NT2030, DE2030 | Yes
| ΔSO2 | Sulphur dioxide | B4c | kg / year | NT2030, DE2030 | Yes
| ΔPM5 | Particulate matter 5 | B4d | kg / year | NT2030, DE2030 | Yes
| ΔPM10 | Particulate matter 10 | B4e | kg / year | NT2030, DE2030 | Yes
| ΔNMVOC | Non-methane volatile organic compounds | B4f | kg / year | NT2030, DE2030 | Yes
| Δlosses | Variation of network losses | B5 | GWh / year | NT2030 | Yes
| Δlosses_monetized | Variation of network losses monetized | B5_SEW | M€ / year | NT2030, DE2030 | Yes
| ΔSoS | Annual reduction in ENS | B6 | MWh / year | NT2030, DE2030 | No
| ΔSoS_monetized | Annual Socio-Economic Welfare increase resulting from reduction in ENS | B6_SEW | M€ / year | NT2030, DE2030 | No

## NT2030_EU
Scenario | NT2030
[16 empty] | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 40 | 44 | 35 | 11 | 14 | 7 | 28 | 37 | 17 | -154 | -99 | -200 | 10 | 0 | 5 | 18 | 0 | 0 | 1 | 497 | 658 | 302 | 1154 | -120 | -12 | -12 | -9 | -6 | -4 | 12 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
4 | Interconnection Portugal-Spain | TOOT | 11 | 16 | 4 | 5 | 7 | 2 | 6 | 9 | 2 | -68 | -25 | -106 | 5 | 0 | 2 | 8 | 0 | 0 | 1 | 115 | 174 | 33 | 0 | -29 | 3 | -59 | -1 | 0 | 1 | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
16 | Biscay Gulf | TOOT | 266 | 268 | 263 | 95 | 106 | 86 | 116 | 127 | 107 | -1358 | -1225 | -1512 | 403 | 0 | 41 | 162 | 0 | 12 | 48 | 2061 | 2244 | 1847 | 0 | -817 | -80 | -153 | -68 | -43 | -24 | 1717 | 75 | N/A | N/A | N/A | N/A | N/A | N/A
26 | Reschenpass Interconnector Project | TOOT | 11 | 15 | 6 | 12 | 17 | 8 | 2 | 3 | 1 | -176 | -113 | -244 | 15 | 0 | 5 | 21 | 0 | 0 | 2 | 30 | 53 | 20 | 0 | -277 | -20 | -152 | -19 | -13 | -6 | 66 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
28 | Italy-Montenegro | PINT | 8 | 10 | 7 | 5 | 6 | 4 | 6 | 9 | 4 | -70 | -61 | -79 | 4 | 0 | 2 | 8 | 0 | 0 | 1 | 114 | 162 | 67 | 0 | -92 | -7 | -71 | -6 | -5 | -2 | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
29 | Italy-Tunisia | TOOT | 15 | 25 | 5 | -82 | -82 | -82 | 9 | 11 | 7 | 1178 | 1178 | 1177 | 17 | 0 | 0 | 0 | 0 | 1 | 2 | 165 | 201 | 128 | 0 | 1124 | 129 | 69 | 89 | 57 | 39 | -12 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
33 | Central Northern Italy | TOOT | 3 | 3 | 2 | 1 | 2 | -1 | 3 | 3 | 3 | -13 | 10 | -35 | 28 | 0 | 0 | 1 | 0 | 1 | 3 | 51 | 54 | 49 | 0 | -25 | 0 | -24 | -2 | -2 | 0 | 54 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
35 | CZ Southwest-east corridor | PINT | 47 | 50 | 42 | 28 | 31 | 26 | 13 | 20 | 10 | -406 | -378 | -436 | 60 | 0 | 12 | 48 | 0 | 2 | 7 | 239 | 363 | 170 | 0 | -402 | -50 | 22 | -33 | -21 | -15 | 313 | 11 | N/A | N/A | N/A | N/A | N/A | N/A
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 12 | 15 | 9 | 7 | 7 | 6 | 5 | 7 | 4 | -97 | -88 | -102 | N/A | 0 | 3 | 12 | N/A | N/A | N/A | 90 | 131 | 64 | 0 | -129 | -10 | -59 | -11 | -8 | -3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 41 | 44 | 36 | 17 | 18 | 16 | 13 | 21 | 10 | -241 | -224 | -253 | 42 | 0 | 7 | 29 | 0 | 1 | 5 | 237 | 385 | 176 | 0 | -342 | -27 | -156 | -26 | -17 | -8 | 292 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 0 | 0 | 0 | -14 | -7 | -20 | 6 | 12 | 1 | 193 | 291 | 95 | 19 | 0 | 0 | 0 | 0 | 1 | 2 | 100 | 212 | 19 | 0 | 307 | 32 | 50 | 26 | 17 | 10 | 104 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
85 | Integration of RES in Alentejo | TOOT | 29 | 35 | 24 | 4 | 7 | 0 | 34 | 43 | 29 | -50 | -3 | -97 | 41 | 0 | 2 | 6 | 0 | 1 | 5 | 595 | 760 | 531 | 442 | -29 | -2 | -27 | 0 | 0 | -1 | 218 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
94 | GerPol Improvements | TOOT | 102 | 104 | 100 | 122 | 127 | 115 | 16 | 20 | 11 | -1742 | -1643 | -1809 | N/A | 0 | 52 | 207 | N/A | N/A | N/A | 293 | 365 | 188 | 0 | -3239 | -1 | -4624 | -182 | -122 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
103 | Reinforcements Ring NL phase I | TOOT | 9 | 11 | 5 | 5 | 5 | 5 | 2 | 3 | 1 | -74 | -70 | -77 | -14 | 0 | 2 | 9 | 0 | 0 | -2 | 42 | 61 | 22 | 0 | -39 | -9 | 58 | -4 | -2 | -3 | -85 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
107 | Celtic Interconnector | TOOT | 147 | 149 | 144 | 27 | 28 | 27 | 89 | 97 | 79 | -388 | -380 | -403 | 165 | 0 | 12 | 46 | 0 | 5 | 20 | 1594 | 1725 | 1470 | 0 | -445 | -39 | -125 | -35 | -22 | -12 | 718 | 29 | N/A | N/A | N/A | N/A | N/A | N/A
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 42 | 43 | 40 | 16 | 17 | 15 | 3 | 3 | 2 | -229 | -221 | -238 | 22 | 0 | 7 | 27 | 0 | 1 | 3 | 46 | 59 | 32 | 0 | -780 | -13 | -2192 | -36 | -60 | -5 | 93 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 656 | 656 | 656 | 155 | 155 | 155 | 798 | 798 | 798 | -2220 | -2220 | -2220 | 6 | 0 | 67 | 264 | 0 | 0 | 1 | 13675 | 13675 | 13675 | 3500 | -2184 | -174 | -1134 | -149 | -96 | -53 | 826 | 40 | 0 | 0 | 0 | 0 | 0 | 0
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 48 | 53 | 39 | 34 | 38 | 30 | 4 | 6 | 0 | -486 | -429 | -547 | 110 | 0 | 15 | 58 | 0 | 3 | 13 | 65 | 114 | 0 | 0 | -542 | -51 | -134 | -44 | -28 | -15 | 359 | 21 | N/A | N/A | N/A | N/A | N/A | N/A
123 | LitPol Link Stage 2 | TOOT | 151 | 170 | 123 | 160 | 160 | 160 | 20 | 31 | 12 | -2289 | -2288 | -2290 | -16 | 0 | 69 | 272 | 0 | 0 | 0 | 359 | 576 | 207 | 0 | -1052 | -30 | 1728 | -94 | 22 | -7 | -36 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
124 | NordBalt phase 2 | PINT | 22 | 27 | 14 | 21 | 24 | 17 | 5 | 6 | 3 | -302 | -239 | -343 | -22 | 0 | 9 | 36 | 0 | -1 | 0 | 82 | 113 | 56 | 0 | -422 | -13 | -2937 | -36 | -108 | -4 | -120 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
126 | SE North-south short-term reinforcements | TOOT | 62 | 78 | 46 | 22 | 30 | 16 | 2 | 4 | 1 | -318 | -226 | -424 | 27 | 0 | 10 | 38 | 0 | 1 | 3 | 43 | 68 | 18 | 0 | -732 | -33 | -985 | -43 | -38 | -10 | 183 | 6 | N/A | N/A | N/A | N/A | N/A | N/A
127 | Central Southern Italy | TOOT | 2 | 4 | 2 | 1 | 2 | -2 | 3 | 4 | 2 | -8 | 24 | -32 | 47 | 0 | 0 | 1 | 0 | 1 | 6 | 50 | 68 | 31 | 0 | -36 | 0 | -71 | 0 | 0 | 0 | 126 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 245 | 245 | 245 | 12 | 12 | 12 | 69 | 69 | 69 | -421 | -421 | -421 | -8 | 0 | 13 | 50 | 0 | 0 | -1 | 686 | 686 | 686 | 0 | -691 | -691 | -731 | -44 | -29 | -6 | 230 | -3 | 0 | 0 | 0 | 0 | 0 | 0
132 | HVDC Line A-North | TOOT | 901 | 901 | 901 | 42 | 42 | 42 | 285 | 285 | 285 | -1503 | -1503 | -1503 | -118 | 0 | 45 | 179 | 0 | -4 | -14 | 2846 | 2846 | 2846 | 0 | -2419 | -2419 | -2558 | -150 | -99 | -23 | 588 | -23 | 0 | 0 | 0 | 0 | 0 | 0
138 | Black Sea Corridor | TOOT | 11 | 14 | 8 | 3 | 7 | 0 | 1 | 1 | 0 | -36 | 6 | -103 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 9 | 18 | 6 | 0 | -38 | -3 | -5 | -3 | -2 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
142 | CSE4 | TOOT | 2 | 5 | 0 | 1 | 3 | 0 | 0 | 1 | 0 | -19 | -6 | -49 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 7 | 25 | -3 | 0 | -15 | 6 | -83 | 0 | 0 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
144 | Mid Continental East corridor | TOOT | 12 | 15 | 10 | 3 | 6 | 1 | 1 | 2 | 1 | -45 | -15 | -90 | -29 | 0 | 1 | 5 | 0 | -1 | -3 | 21 | 34 | 10 | 0 | -106 | -8 | -59 | -6 | -4 | -2 | -105 | -5 | N/A | N/A | N/A | N/A | N/A | N/A
150 | Italy-Slovenia | light PINT | 9 | 14 | 1 | 10 | 13 | 7 | 2 | 3 | 0 | -143 | -105 | -183 | 66 | 0 | 4 | 17 | 0 | 2 | 8 | 30 | 58 | 0 | 0 | -148 | -8 | -144 | -8 | -6 | -3 | 202 | 12 | N/A | N/A | N/A | N/A | N/A | N/A
153 | France-Alderney-Britain | PINT | 44 | 50 | 37 | 17 | 19 | 16 | 15 | 18 | 10 | -245 | -227 | -267 | 144 | 0 | 7 | 29 | 0 | 4 | 17 | 278 | 340 | 177 | 0 | -449 | -24 | -389 | -29 | -20 | -7 | 700 | 30 | N/A | N/A | N/A | N/A | N/A | N/A
170 | Baltic States Synchronization with Continental Europe | TOOT | 189 | 191 | 188 | 219 | 230 | 204 | 31 | 47 | 20 | -3133 | -2917 | -3289 | 1 | 0 | 94 | 373 | 0 | 0 | 0 | 567 | 867 | 354 | 0 | -2501 | -50 | 497 | -180 | -15 | -13 | 97 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
174 | Greenconnector | PINT | 34 | 45 | 24 | 40 | 40 | 39 | 2 | 4 | 0 | -565 | -559 | -571 | 115 | 0 | 17 | 67 | 0 | 3 | 14 | 27 | 69 | 3 | 0 | -636 | -57 | -254 | -47 | -30 | -17 | 129 | 10 | N/A | N/A | N/A | N/A | N/A | N/A
176 | Hansa PowerBridge I | TOOT | 137 | 142 | 132 | 74 | 74 | 73 | 9 | 10 | 8 | -1051 | -1046 | -1057 | N/A | 0 | 32 | 125 | N/A | N/A | N/A | 156 | 168 | 143 | 0 | -1155 | -93 | -303 | -85 | -47 | -28 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
183 | DKW-DE, Westcoast | TOOT | 24 | 36 | 11 | 31 | 37 | 22 | 3 | 9 | 0 | -446 | -313 | -534 | N/A | 0 | 13 | 53 | N/A | N/A | N/A | 60 | 169 | 2 | 0 | -239 | -47 | 324 | -31 | -19 | -14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
186 | East of Austria | TOOT | 281 | 292 | 267 | 86 | 92 | 82 | 272 | 273 | 272 | -1211 | -1172 | -1260 | -19 | 0 | 37 | 146 | 0 | -1 | -2 | 4983 | 5115 | 4820 | 2000 | -1396 | -126 | -522 | -103 | -66 | -38 | -47 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
187 | St. Peter (AT) - Pleinting (DE) | PINT | 83 | 87 | 78 | 34 | 41 | 26 | 26 | 28 | 24 | -489 | -374 | -585 | 103 | 0 | 15 | 58 | 0 | 3 | 12 | 463 | 492 | 417 | 0 | -794 | -58 | -411 | -61 | -40 | -17 | 711 | 21 | N/A | N/A | N/A | N/A | N/A | N/A
190 | NorthConnect | TOOT | 10 | 31 | 0 | 53 | 64 | 43 | 6 | 10 | 1 | -756 | -609 | -920 | 26 | 0 | 23 | 90 | 0 | 1 | 3 | 89 | 164 | -39 | 0 | -928 | -81 | -303 | -72 | -45 | -24 | 282 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 47 | 54 | 41 | 31 | 35 | 28 | 14 | 18 | 11 | -449 | -403 | -496 | 35 | 0 | 13 | 53 | 0 | 1 | 4 | 255 | 329 | 183 | 0 | 1574 | -37 | 3316 | 55 | 52 | -8 | 250 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 6 | 10 | 1 | 6 | 9 | 3 | 1 | 5 | 0 | -81 | -48 | -127 | 4 | 0 | 2 | 10 | 0 | 0 | 0 | 24 | 83 | 1 | 0 | -48 | -9 | 120 | -7 | -2 | -2 | 6 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
219 | EuroAsia Interconnector | TOOT | 81 | 89 | 72 | -35 | -7 | -63 | 1 | 1 | 1 | 498 | 897 | 98 | 220 | 0 | 0 | 0 | 0 | 7 | 26 | 12 | 14 | 9 | 0 | 3167 | 72 | 4013 | 188 | 136 | 23 | 708 | 41 | N/A | N/A | N/A | N/A | N/A | N/A
225 | 2nd interconnector Belgium - Germany | light PINT | 28 | 29 | 25 | 9 | 12 | 7 | 10 | 13 | 8 | -135 | -102 | -171 | N/A | 0 | 4 | 16 | N/A | N/A | N/A | 185 | 236 | 136 | 0 | -162 | -20 | -6 | -13 | -9 | -6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
227 | Transbalkan Corridor | TOOT | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | -2 | 5 | -9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 0 | 0 | -20 | 2 | -57 | 0 | 0 | 1 | -1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
228 | Muhlbach - Eichstetten | TOOT | 22 | 26 | 15 | 10 | 12 | 5 | 8 | 10 | 6 | -142 | -72 | -178 | 37 | 0 | 4 | 17 | 0 | 1 | 4 | 147 | 179 | 102 | 0 | -293 | -13 | -243 | -19 | -12 | -4 | 183 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
230 | GerPol Power Bridge I | TOOT | 306 | 324 | 290 | 416 | 430 | 403 | 29 | 30 | 28 | -5947 | -5754 | -6141 | N/A | 0 | 178 | 708 | N/A | N/A | N/A | 495 | 517 | 474 | 0 | -8070 | 5 | -10499 | -508 | -324 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
231 | Beznau - Tiengen | PINT | 13 | 19 | 8 | 13 | 17 | 8 | 17 | 24 | 11 | -185 | -115 | -240 | N/A | 0 | 6 | 22 | N/A | N/A | N/A | 309 | 453 | 197 | 0 | -253 | -29 | -10 | -21 | -14 | -9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 2032 | 2032 | 2032 | 88 | 88 | 88 | 652 | 652 | 652 | -3160 | -3160 | -3160 | -167 | 0 | 95 | 376 | 0 | -5 | -20 | 6516 | 6516 | 6516 | 0 | -4554 | -4554 | -3974 | -310 | -203 | -59 | 970 | -35 | 0 | 0 | 0 | 0 | 0 | 0
239 | Fenno-Skan 1 renewal | light PINT | 12 | 13 | 12 | 5 | 9 | 3 | 3 | 9 | 0 | -73 | -42 | -129 | N/A | 0 | 2 | 9 | N/A | N/A | N/A | 60 | 167 | 7 | 0 | -120 | -6 | -377 | -5 | -11 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 5 | 9 | 3 | 1 | 5 | -3 | 1 | 2 | 0 | -19 | 40 | -74 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 15 | 32 | 3 | 0 | -118 | -14 | -7 | -10 | -7 | -4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
244 | Vigy - Uchtelfangen area | PINT | 113 | 118 | 109 | 49 | 55 | 44 | 41 | 55 | 29 | -696 | -629 | -790 | 228 | 0 | 21 | 83 | 0 | 7 | 27 | 728 | 1024 | 494 | 0 | -1181 | -58 | -986 | -80 | -53 | -18 | 1053 | 41 | N/A | N/A | N/A | N/A | N/A | N/A
245 | Upgrade Meeden - Diele | TOOT | 3 | 3 | 2 | 3 | 3 | 3 | 1 | 1 | 1 | -38 | -38 | -39 |  | 0 | 1 | 5 |  |  |  | 16 | 17 | 15 | 0 | 40 | 3 | 17 | 2 | 1 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
247 | AQUIND Interconnector | PINT | 63 | 71 | 51 | 28 | 38 | 22 | 21 | 27 | 16 | -406 | -310 | -541 | 187 | 0 | 12 | 48 | 0 | 6 | 22 | 379 | 501 | 281 | 0 | -550 | -31 | -459 | -34 | -22 | -10 | 745 | 36 | N/A | N/A | N/A | N/A | N/A | N/A
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 9 | 11 | 8 | 7 | 10 | 0 | 1 | 2 | 0 | -96 | 6 | -141 | -2 | 0 | 3 | 11 | 0 | 0 | 0 | 16 | 43 | 0 | 0 | -153 | -15 | -47 | -13 | -9 | -4 | -4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -10 | 0 | 0 | 2 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -35 | -2 | 0 | 0 | 0 | 0 | 0 | 0
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 10 | 16 | 5 | 11 | 17 | 6 | 1 | 2 | 0 | -153 | -86 | -241 | 144 | 0 | 5 | 18 | 0 | 4 | 17 | 21 | 43 | 5 | 0 | -162 | -22 | 42 | -15 | -10 | -6 | 752 | 29 | N/A | N/A | N/A | N/A | N/A | N/A
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 90 | 90 | 90 | 5 | 5 | 5 | 27 | 27 | 27 | -196 | -196 | -196 | 203 | 0 | 6 | 23 | 0 | 6 | 24 | 275 | 275 | 275 | 0 | -322 | -322 | -259 | -30 | -20 | -2 | -394 | 30 | 0 | 0 | 0 | 0 | 0 | 0
259 | HU-RO | PINT | 12 | 15 | 10 | 4 | 6 | 2 | 1 | 2 | 0 | -56 | -30 | -92 | 139 | 0 | 2 | 7 | 0 | 4 | 17 | 16 | 42 | 7 | 0 | -2412 | 3 | -3884 | -131 | -101 | -1 | 335 | 22 | N/A | N/A | N/A | N/A | N/A | N/A
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 58 | 63 | 50 | 23 | 28 | 13 | 5 | 11 | 0 | -322 | -187 | -403 | 148 | 0 | 10 | 38 | 0 | 4 | 18 | -840 | 184 | -1864 | 2000 | -462 | -33 | -236 | -31 | -19 | -10 | 466 | 25 | N/A | N/A | N/A | N/A | N/A | N/A
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 20 | 22 | 17 | 4 | 5 | 3 | 17 | 20 | 13 | -62 | -44 | -76 | N/A | 0 | 2 | 7 | N/A | N/A | N/A | 310 | 352 | 228 | 0 | 110 | 2 | 129 | 6 | 3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
263 | Lake Constance East | light PINT | 70 | 80 | 64 | 36 | 43 | 30 | 25 | 25 | 25 | -515 | -432 | -621 | N/A | 0 | 15 | 61 | N/A | N/A | N/A | 442 | 448 | 435 | 0 | -913 | -57 | -573 | -68 | -44 | -17 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
267 | Hansa PowerBridge II | light PINT | 112 | 148 | 68 | 65 | 65 | 64 | 9 | 15 | 6 | -922 | -920 | -924 | N/A | 0 | 28 | 110 | N/A | N/A | N/A | 160 | 285 | 96 | 0 | -1038 | -89 | 7 | -75 | -33 | -27 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 125 | 138 | 108 | 43 | 49 | 38 | 57 | 63 | 47 | -615 | -544 | -699 | 376 | 0 | 18 | 73 | 0 | 11 | 45 | 1007 | 1165 | 834 | 0 | -485 | -49 | -97 | -39 | -25 | -15 | 1511 | 71 | N/A | N/A | N/A | N/A | N/A | N/A
276 | FR-ES project -Navarra-Landes | PINT | 125 | 138 | 108 | 43 | 49 | 38 | 57 | 63 | 47 | -615 | -544 | -699 | 377 | 0 | 18 | 73 | 0 | 11 | 45 | 1007 | 1165 | 834 | 0 | -485 | -49 | -97 | -39 | -25 | -15 | 1511 | 71 | N/A | N/A | N/A | N/A | N/A | N/A
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 53 | 56 | 50 | 25 | 29 | 21 | 15 | 20 | 12 | -362 | -294 | -407 | 112 | 0 | 11 | 43 | 0 | 3 | 13 | 269 | 370 | 205 | 0 | -615 | -31 | -515 | -40 | -27 | -10 | 444 | 20 | N/A | N/A | N/A | N/A | N/A | N/A
283 | TuNur Italy | PINT | 1 | 2 | 0 | 209 | 271 | 129 | 704 | 732 | 677 | -2993 | -1837 | -3868 | -111 | 0 | 90 | 356 | 0 | -3 | -13 | 12685 | 12885 | 12486 | 4900 | -3624 | -416 | -183 | -289 | -184 | -125 | -342 | -20 | N/A | N/A | N/A | N/A | N/A | N/A
285 | GridLink | PINT | 44 | 50 | 37 | 17 | 19 | 16 | 15 | 18 | 10 | -245 | -227 | -267 | 199 | 0 | 7 | 29 | 0 | 6 | 24 | 278 | 340 | 177 | 0 | -449 | -24 | -389 | -29 | -20 | -7 | 787 | 38 | N/A | N/A | N/A | N/A | N/A | N/A
286 | Greenlink | PINT | 27 | 38 | 19 | 14 | 15 | 13 | 27 | 34 | 23 | -201 | -182 | -212 | 20 | 0 | 6 | 24 | 0 | 1 | 2 | 488 | 627 | 397 | 0 | 68 | -5 | 141 | 5 | 4 | -2 | 118 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
293 | Southern Aegean Interconnector | PINT | 85 | 87 | 81 | 28 | 31 | 25 | 77 | 80 | 75 | -407 | -354 | -447 | 91 | 0 | 12 | 48 | 0 | 3 | 11 | 1357 | 1381 | 1327 | 582 | -2568 | -43 | -3606 | -141 | -106 | -15 | 201 | 14 | N/A | N/A | N/A | N/A | N/A | N/A
297 | BRABO II + III | TOOT | 20 | 22 | 17 | 4 | 5 | 3 | 17 | 20 | 13 | -62 | -44 | -76 | 93 | 0 | 2 | 7 | 0 | 3 | 11 | 310 | 352 | 228 | 0 | -110 | -2 | -129 | -6 | -3 | -1 | 390 | 17 | N/A | N/A | N/A | N/A | N/A | N/A
299 | SACOI3 | TOOT | 109 | 114 | 103 | 32 | 35 | 30 | 4 | 6 | 2 | -457 | -426 | -501 | 35 | 0 | 14 | 54 | 0 | 1 | 4 | 73 | 115 | 39 | 0 | -1000 | 19 | -2656 | -8 | -156 | -1 | 113 | 6 | N/A | N/A | N/A | N/A | N/A | N/A
309 | NeuConnect | TOOT | 58 | 65 | 48 | 62 | 65 | 59 | 9 | 14 | 0 | -886 | -849 | -927 | 149 | 0 | 27 | 105 | 0 | 4 | 18 | 155 | 255 | 0 | 0 | -957 | -77 | -384 | -73 | -46 | -23 | 539 | 27 | N/A | N/A | N/A | N/A | N/A | N/A
312 | St. Peter (AT) - Tauern (AT) | TOOT | 166 | 179 | 158 | 57 | 60 | 54 | 57 | 68 | 47 | -1036 | -828 | -1294 | 105 | 0 | 25 | 97 | 0 | 3 | 13 | 1029 | 1255 | 820 | 0 | -1417 | -107 | -659 | -107 | -68 | -32 | 893 | 22 | N/A | N/A | N/A | N/A | N/A | N/A
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 157 | 162 | 149 | 69 | 81 | 58 | 54 | 68 | 40 | -981 | -828 | -1160 | 129 | 0 | 29 | 117 | 0 | 4 | 15 | 956 | 1255 | 684 | 0 | -1417 | -107 | -659 | -107 | -68 | -32 | 977 | 27 | N/A | N/A | N/A | N/A | N/A | N/A
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 1 | 2 | 0 | -1 | 0 | -2 | 0 | 1 | 0 | 14 | 34 | 3 | -6 | 0 | 0 | 0 | N/A | 0 | N/A | 8 | 18 | 1 | 0 | -45 | 4 | -89 | -4 | -2 | 1 | -10 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 5 | 9 | 1 | 0 | 1 | -1 | 1 | 2 | 0 | 3 | 18 | -10 | -7 | 0 | 0 | 0 | 0 | 0 | -1 | 14 | 34 | 0 | 0 | 0 | 1 | -3 | 0 | 1 | 0 | -15 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
325 | Obersielach (AT) - Podlog (SI) | PINT | 20 | 23 | 14 | 19 | 24 | 13 | 2 | 5 | 2 | -270 | -182 | -337 | 50 | 0 | 8 | 32 | 0 | 1 | 6 | 43 | 92 | 28 | 0 | -337 | -31 | -142 | -25 | -17 | -9 | 146 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
328 | Interconnector DE-LUX | TOOT | 0 | 1 | 0 | -1 | 0 | -2 | 0 | 1 | 0 | 8 | 34 | -4 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 5 | 17 | -1 | 0 | -1 | 2 | -14 | 1 | 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 416 | 416 | 416 | 149 | 149 | 149 | 324 | 324 | 324 | -2134 | -2134 | -2134 | 8 | 0 | 64 | 254 | 0 | 0 | 1 | 5561 | 5561 | 5561 | 0 | -1942 | -226 | -54 | -156 | -99 | -68 | 38 | 1 | 0 | 0 | 0 | 0 | 0 | 0
330 | 4th 400kV CZ-SK interconnector | light PINT | 4 | 7 | 0 | 2 | 4 | 1 | 1 | 1 | 0 | -34 | -13 | -53 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 11 | 24 | 3 | 0 | -53 | 2 | -98 | -5 | -3 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
333 | PST Foretaille | PINT | 32 | 36 | 26 | 46 | 52 | 41 | 1 | 2 | 0 | -661 | -586 | -740 | 119 | 0 | 20 | 79 | 0 | 4 | 14 | 19 | 45 | 3 | 0 | -791 | -71 | -289 | -59 | -38 | -21 | 634 | 24 | N/A | N/A | N/A | N/A | N/A | N/A
335 | Project 335 - North Sea Wind Power Hub | light PINT | 819 | 904 | 721 | 690 | 708 | 680 | 3163 | 3313 | 2987 | -9855 | -9714 | -10115 | N/A | 0 | 296 | 1173 | N/A | N/A | N/A | 56773 | 57751 | 55772 | 12000 | -10329 | -848 | -4984 | -729 | -475 | -258 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
338 | Adriatic HVDC link | PINT | 14 | 16 | 12 | 8 | 8 | 7 | 7 | 11 | 3 | -109 | -103 | -114 | -10 | 0 | 3 | 13 | 0 | 0 | -1 | 129 | 205 | 54 | 0 | -155 | -12 | -67 | -14 | -10 | -3 | 2 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
339 | Italian HVDC tri-terminal link | PINT | 3 | 6 | 0 | 4 | 5 | 4 | 3 | 4 | 2 | -64 | -61 | -67 | 145 | 0 | 2 | 8 | 0 | 4 | 17 | 51 | 71 | 31 | 0 | -50 | -8 | -3 | -4 | -3 | -2 | -190 | 22 | N/A | N/A | N/A | N/A | N/A | N/A
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 203 | 203 | 203 | 73 | 73 | 73 | 146 | 146 | 146 | -1041 | -1041 | -1041 | -87 | 0 | 31 | 124 | 0 | -3 | -10 | 2509 | 2509 | 2509 | 0 | -920 | -107 | -25 | -74 | -47 | -15 | -375 | -17 | 0 | 0 | 0 | 0 | 0 | 0
341 | North CSE Corridor | PINT | 1 | 3 | 0 | 0 | 2 | -2 | 0 | 0 | 0 | 3 | 35 | -27 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 4 | 7 | 1 | 0 | -48 | -8 | 29 | -6 | -4 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
342 | Central Balkan Corridor | PINT | 3 | 7 | 0 | 3 | 9 | -1 | 0 | 1 | 0 | -38 | 8 | -129 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 6 | 16 | 1 | 0 | 2 | -3 | 43 | -1 | -1 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
343 | CSE1 New | PINT | 2 | 3 | 1 | 1 | 2 | 0 | 0 | 1 | 0 | -18 | -3 | -32 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 8 | 13 | 1 | 0 | -69 | -8 | -11 | -6 | -4 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
344 | Reinforcements Ring NL phase II | PINT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
345 | 3rd circuit Diemen-Lelystad-Ens | PINT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
346 | ZuidWest380 NL Oost | PINT | 14 | 16 | 12 | 1 | 2 | 0 | 10 | 12 | 6 | -21 | -2 | -35 | -188 | 0 | 1 | 3 | 0 | -6 | -22 | 182 | 227 | 110 | 0 | -98 | -4 | -93 | -7 | -5 | -1 | -1723 | -40 | N/A | N/A | N/A | N/A | N/A | N/A
347 | 3rd circuit Krimpen a/d IJssel - Geertruidenberg | PINT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
348 | NoordWest380 NL | TOOT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
349 | MaresConnect | PINT | 32 | 34 | 30 | 20 | 22 | 18 | 40 | 47 | 36 | -287 | -257 | -316 | 60 | 0 | 9 | 34 | 0 | 2 | 7 | 719 | 875 | 632 | 0 | 68 | -5 | 141 | 5 | 4 | -2 | 254 | 10 | N/A | N/A | N/A | N/A | N/A | N/A
350 | South Balkan Corridor | TOOT | 2 | 3 | 2 | 1 | 4 | -2 | 0 | 0 | 0 | -11 | 22 | -64 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 0 | 4 | -2 | 0 | 38 | 3 | 30 | 3 | 2 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 32 | 42 | 24 | 18 | 23 | 15 | 2 | 4 | 1 | -254 | -209 | -325 | 22 | 0 | 8 | 30 | 0 | 1 | 3 | 45 | 78 | 17 | 0 | -357 | -36 | -97 | -26 | -17 | -11 | 116 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 1 | 3 | 0 | 1 | 4 | -1 | 0 | 1 | 0 | -15 | 21 | -62 | N/A | 0 | 0 | 2 | N/A | N/A | N/A | 6 | 15 | 1 | 0 | 17 | -3 | 38 | 2 | 1 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 15 | 16 | 14 | 2 | 3 | 0 | 10 | 12 | 6 | -22 | -2 | -37 | 122 | 0 | 1 | 3 | 0 | 4 | 14 | 182 | 227 | 109 | 0 | -85 | -5 | -59 | -7 | -5 | -1 | 108 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
378 | Transformer Gatica | TOOT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | [12 empty] | N/A | 0 | 0 | 0 | N/A | N/A | N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 876 | 876 | 876 | 34 | 34 | 34 | 267 | 267 | 267 | -1209 | -1209 | -1209 | -61 | 0 | 36 | 144 | 0 | 2 | 7 | 2665 | 2665 | 2665 | 0 | -1745 | -1745 | -1632 | -107 | -70 | -24 | -250 | 12 | 0 | 0 | 0 | 0 | 0 | 0
1039 | SE North-south long-term reinforcements | light PINT | 8 | 10 | 4 | 8 | 11 | 5 | 3 | 7 | 1 | -110 | -78 | -159 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 59 | 140 | 13 | 0 | -129 | -9 | -127 | -8 | -7 | -3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1040 | LirIC | PINT | 37 | 39 | 35 | 15 | 18 | 13 | 14 | 16 | 11 | -220 | -186 | -251 | -8 | 0 | 7 | 26 | 0 | 0 | -1 | 248 | 300 | 194 | 0 | -254 | -26 | -58 | -21 | -14 | -8 | 153 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1041 | GREGY Green Energy Interconnector | PINT | 52 | 62 | 47 | 45 | 100 | -6 | 1 | 3 | 0 | -637 | 86 | -1434 | 253 | 0 | 19 | 76 | 0 | 8 | 30 | 20 | 50 | 3 | 0 | -1314 | -157 | -5 | -105 | -67 | -47 | 723 | 51 | N/A | N/A | N/A | N/A | N/A | N/A
1042 | Offshore Wind LT 1 | PINT | 82 | 98 | 66 | 15 | 23 | 10 | 133 | 149 | 115 | -220 | -147 | -333 | -8 | 0 | 7 | 26 | 0 | 0 | 0 | 2340 | 2581 | 2112 | 700 | -165 | -8 | -838 | -13 | -32 | -2 | -153 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1046 | Finnish North-South reinforcement | PINT | 10 | 10 | 10 | 0 | 0 | 0 | 10 | 10 | 10 | -4 | -4 | -4 | -81 | 0 | 0 | 1 | 0 | -2 | -10 | 186 | 186 | 186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -624 | -18 | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 17 | 19 | 14 | 7 | 8 | 6 | 3 | 4 | 3 | -100 | -88 | -118 |  | 0 | 3 | 12 |  |  |  | 62 | 70 | 52 | 0 | -58 | -17 | 127 | -8 | -5 | -5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 30 | 31 | 29 | 77 | 81 | 71 | 1 | 2 | 0 | -1097 | -1014 | -1163 | 759 | 0 | 33 | 131 | 0 | 23 | 90 | 16 | 40 | 6 | 0 | -1529 | -163 | -229 | -120 | -77 | -49 | 2158 | 144 | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 48 | 53 | 39 | 40 | 45 | 38 | 1 | 4 | 0 | -579 | -547 | -637 | 28 | 0 | 17 | 69 | 0 | 1 | 3 | 23 | 69 | 0 | 0 | -734 | -62 | -339 | -51 | -32 | -19 | 274 | 15 | N/A | N/A | N/A | N/A | N/A | N/A
1050 | Tarchon Energy Ltd | PINT | 49 | 57 | 40 | 54 | 57 | 53 | 8 | 14 | 0 | -774 | -753 | -816 | 106 | 0 | 23 | 92 | 0 | 3 | 13 | 147 | 256 | 0 | 0 | -792 | -71 | -257 | -62 | -40 | -21 | 430 | 20 | N/A | N/A | N/A | N/A | N/A | N/A
1051 | Aminth Energy Ltd | PINT | 65 | 66 | 63 | 27 | 33 | 23 | 7 | 11 | 0 | -381 | -331 | -468 | 34 | 0 | 11 | 45 | 0 | 1 | 4 | 130 | 201 | 0 | 0 | -590 | -32 | -572 | -32 | -22 | -10 | 120 | 6 | N/A | N/A | N/A | N/A | N/A | N/A
1052 | Lienz (AT) - Obersielach (AT) | PINT | 23 | 33 | 16 | 19 | 24 | 13 | 2 | 5 | 0 | -242 | -182 | -337 | 38 | 0 | 8 | 33 | 0 | 1 | 5 | 44 | 92 | 10 | 0 | -316 | -27 | -138 | -24 | -16 | -8 | 128 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 42 | 45 | 36 | 17 | 18 | 16 | 14 | 21 | 10 | -242 | -224 | -261 | 57 | 0 | 7 | 29 | 0 | 2 | 7 | 258 | 385 | 176 | 0 | -351 | -27 | -183 | -27 | -18 | -8 | 341 | 11 | N/A | N/A | N/A | N/A | N/A | N/A
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 90 | 117 | 66 | -92 | -78 | -111 | 0 | 0 | 0 | 1313 | 1586 | 1116 | 147 | 0 | 0 | 0 | 0 | 4 | 17 | 0 | 6 | -8 | 0 | 1078 | 115 | 167 | 85 | 55 | 35 | 373 | 26 | N/A | N/A | N/A | N/A | N/A | N/A
1058 | HVDC Interconnector DE-CH | light PINT | 23 | 27 | 20 | 30 | 34 | 24 | 28 | 38 | 23 | -430 | -344 | -479 | N/A | 0 | 13 | 51 | N/A | N/A | N/A | 404 | 410 | 397 | 0 | -664 | -46 | -356 | -50 | -32 | -14 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1059 | Southern Italy | PINT | 6 | 12 | 1 | 1 | 2 | 0 | 1 | 1 | 0 | -11 | 4 | -35 | -13 | 0 | 0 | 1 | 0 | 0 | -2 | 11 | 15 | 8 | 0 | 38 | -3 | 61 | 4 | 2 | -1 | -37 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1063 | ZuidWest380 West | PINT | 19 | 25 | 15 | 2 | 4 | 1 | 8 | 12 | 5 | -33 | -20 | -51 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 145 | 227 | 86 | 0 | -75 | -6 | -48 | -6 | -5 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1066 | Bulgaria - Turkey | light PINT | 79 | 81 | 78 | -206 | -195 | -214 | 1 | 2 | 0 | 2945 | 3058 | 2782 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 19 | 30 | 0 | 0 | 2764 | 304 | 278 | 218 | 139 | 91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 40 | 41 | 39 | -108 | -104 | -113 | 1 | 1 | 0 | 1539 | 1608 | 1489 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 8 | 17 | -2 | 0 | 1501 | 165 | 167 | 118 | 75 | 49 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1068 | LaSGo Link | light PINT | 24 | 30 | 18 | 23 | 26 | 21 | 5 | 8 | 3 | -323 | -293 | -377 | -1 | 0 | 10 | 38 | 0 | 0 | 0 | 89 | 142 | 48 | 0 | -461 | -19 | -3143 | -40 | -118 | -6 | 34 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1074 | Pannonian Corridor | PINT | 5 | 8 | 3 | 1 | 5 | -4 | 1 | 2 | 1 | -10 | 56 | -72 | 113 | 0 | 0 | 1 | 0 | 3 | 13 | 19 | 30 | 12 | 0 | -98 | -14 | 21 | -9 | -6 | -4 | 247 | 18 | N/A | N/A | N/A | N/A | N/A | N/A
1082 | Sea-Socket | light PINT | 103 | 112 | 96 | 24 | 26 | 23 | 123 | 127 | 119 | -346 | -336 | -365 | N/A | 0 | 10 | 41 | N/A | N/A | N/A | 2194 | 2285 | 2106 | 700 | -356 | -34 | -112 | -28 | -18 | -10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1085 | Malta-Italy Cable Link No.2 | PINT | 13 | 16 | 10 | 6 | 7 | 6 | 1 | 2 | 0 | -89 | -82 | -95 | 45 | 0 | 3 | 11 | 0 | 1 | 5 | 20 | 46 | 4 | 0 | -67 | -10 | 20 | -7 | -5 | -3 | 96 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 82 | 109 | 61 | 17 | 27 | 11 | 124 | 124 | 124 | -250 | -152 | -387 | -1 | 0 | 7 | 30 | 0 | 0 | 0 | 2064 | 2149 | 1912 | 700 | -185 | -8 | -1193 | -16 | -45 | -2 | -11 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1088 | Off-shore Wind Park in Latvia and Estonia - ELWIND | PINT | 29 | 32 | 24 | 21 | 28 | 16 | 209 | 220 | 189 | -297 | -223 | -393 | -5 | 0 | 9 | 35 | 0 | 0 | 0 | 3626 | 3818 | 3341 | 1000 | -297 | -11 | -1591 | -22 | -58 | -3 | -77 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1092 | Offshore Hybrid HVDC Interconnector BEDK | PINT | 167 | 172 | 162 | 162 | 167 | 155 | 747 | 787 | 699 | -2312 | -2220 | -2390 | 17 | 0 | 69 | 275 | 0 | 1 | 2 | 13173 | 13486 | 12906 | 3000 | -2512 | -203 | -1315 | -175 | -116 | -62 | 898 | 43 | N/A | N/A | N/A | N/A | N/A | N/A
1094 | Estlink 3 | light PINT | 20 | 21 | 20 | 29 | 32 | 25 | 1 | 3 | 0 | -408 | -352 | -457 | -8 | 0 | 12 | 49 | 0 | 0 | 0 | 25 | 55 | 8 | 0 | -355 | -8 | -4204 | -40 | -157 | -2 | -28 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 16 | 18 | 14 | 9 | 11 | 7 | 5 | 14 | 1 | -125 | -100 | -164 | N/A | 0 | 4 | 15 | N/A | N/A | N/A | 99 | 266 | 14 | 0 | -338 | -11 | -895 | -14 | -24 | -4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1096 | Beznau - Mettlen | PINT | 17 | 23 | 10 | 17 | 22 | 14 | 18 | 28 | 14 | -244 | -195 | -312 | N/A | 0 | 7 | 29 | N/A | N/A | N/A | 329 | 514 | 232 | 0 | -234 | -32 | 54 | -22 | -14 | -9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1097 | Upgrade to Konti-Skan | PINT | 79 | 80 | 79 | 31 | 31 | 31 | 11 | 13 | 9 | -440 | -439 | -440 | 135 | 0 | 13 | 52 | 0 | 4 | 16 | 202 | 233 | 171 | 0 | -1049 | -68 | -671 | -68 | -42 | -21 | 470 | 24 | N/A | N/A | N/A | N/A | N/A | N/A
1098 | Offshore Wind LT 2 | PINT | 87 | 98 | 70 | 16 | 23 | 10 | 131 | 149 | 115 | -235 | -148 | -333 | -2 | 0 | 7 | 28 | 0 | 0 | 0 | 2313 | 2579 | 2114 | 700 | -170 | -8 | -846 | -14 | -32 | -2 | -84 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 46 | 51 | 41 | 29 | 30 | 28 | 16 | 19 | 11 | -409 | -397 | -434 | 87 | 0 | 12 | 49 | 0 | 3 | 10 | 280 | 356 | 194 | 0 | -384 | -49 | 37 | -32 | -21 | -15 | 374 | 15 | N/A | N/A | N/A | N/A | N/A | N/A
1102 | Mettlen - Ulrichen | light PINT | 6 | 9 | 4 | 5 | 5 | 5 | 6 | 8 | 4 | -73 | -70 | -76 | N/A | 0 | 2 | 9 | N/A | N/A | N/A | 101 | 156 | 65 | 0 | -48 | -10 | 64 | -6 | -4 | -3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1103 | Bickigen - Chippis | PINT | 12 | 21 | 6 | 12 | 13 | 11 | 13 | 19 | 10 | -174 | -163 | -190 | N/A | 0 | 5 | 21 | N/A | N/A | N/A | 241 | 360 | 163 | 0 | -116 | -22 | 92 | -12 | -8 | -6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1104 | Niederstedem - Roost | PINT | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 6 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 7 | 19 | 1 | 0 | 33 | -1 | 59 | 1 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 16 | 22 | 9 | -39 | -38 | -39 | 1 | 1 | 0 | 553 | 564 | 542 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 9 | 12 | 6 | 0 | 96 | 9 | 38 | 7 | 5 | 3 | 81 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
1106 | Bornholm Energy Island (BEI) | TOOT | 54 | 62 | 50 | 98 | 102 | 94 | 405 | 419 | 388 | -1402 | -1346 | -1459 | 128 | 0 | 42 | 167 | 0 | 4 | 15 | 7025 | 7183 | 6833 | 2000 | -1404 | -109 | -648 | -104 | -66 | -33 | 479 | 24 | N/A | N/A | N/A | N/A | N/A | N/A
1107 | EuroAfrica Interconnector | PINT | 5 | 9 | 0 | 38 | 49 | 26 | 1 | 2 | 0 | -538 | -366 | -697 | -35 | 0 | 16 | 64 | 0 | -1 | -4 | 19 | 36 | 4 | 0 | -314 | -34 | -9 | -24 | -14 | -10 | -109 | -7 | N/A | N/A | N/A | N/A | N/A | N/A
1109 | Basilicata - Campania reinforcements | PINT | 3 | 6 | 0 | 0 | 1 | -1 | 1 | 2 | 1 | 0 | 8 | -8 | -19 | 0 | 0 | 0 | 0 | -1 | -2 | 24 | 35 | 14 | 0 | -17 | -1 | -32 | 0 | -1 | 0 | -47 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1110 | Sicily - Calabria | PINT | 2 | 4 | 0 | -1 | -1 | -1 | 1 | 2 | 0 | 12 | 16 | 8 | 13 | 0 | 0 | 0 | 0 | 0 | 2 | 20 | 32 | 8 | 0 | 13 | -3 | 39 | 0 | 0 | -1 | 30 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1112 | GRITA 2 | PINT | 15 | 20 | 12 | 7 | 14 | 2 | 6 | 8 | 4 | -98 | -22 | -196 | 17 | 0 | 3 | 12 | 0 | 1 | 2 | 103 | 154 | 72 | 0 | -90 | -6 | -78 | -6 | -4 | -2 | 43 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 337 | 337 | 337 | 107 | 107 | 107 | 341 | 341 | 341 | -1464 | -1464 | -1464 | -48 | 0 | 46 | 182 | 0 | -1 | -6 | 6000 | 6000 | 6000 | 3000 | 138 | 0 | 194 | 8 | 6 | 0 | -134 | -7 | N/A | N/A | N/A | N/A | N/A | N/A
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 82 | 82 | 82 | 34 | 34 | 34 | 76 | 76 | 76 | -366 | -366 | -366 | -27 | 0 | 15 | 58 | 0 | -1 | -3 | 1345 | 1345 | 1345 | 750 | 212 | 4 | 245 | 14 | 10 | 2 | -67 | -5 | N/A | N/A | N/A | N/A | N/A | N/A
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 56 | 56 | 56 | 20 | 20 | 20 | 51 | 51 | 51 | -259 | -259 | -259 | -21 | 0 | 9 | 34 | 0 | -1 | -3 | 905 | 905 | 905 | 600 | 34 | 2 | 19 | 4 | 2 | 0 | -64 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 182 | 188 | 175 | 35 | 36 | 32 | 247 | 258 | 233 | -494 | -463 | -515 | 108 | 0 | 15 | 59 | 0 | 3 | 13 | 4406 | 4472 | 4294 | 1050 | -425 | -43 | -87 | -32 | -21 | -13 | 493 | 22 | N/A | N/A | N/A | N/A | N/A | N/A
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 216 | 220 | 212 | 40 | 43 | 34 | 294 | 306 | 275 | -566 | -492 | -614 | 106 | 0 | 17 | 67 | 0 | 3 | 13 | 5233 | 5313 | 5080 | 1250 | -522 | -51 | -179 | -37 | -24 | -16 | 516 | 22 | N/A | N/A | N/A | N/A | N/A | N/A
1124 | Offshore Wind Connection South Britanny | TOOT | 43 | 47 | 38 | 9 | 10 | 7 | 60 | 63 | 55 | -123 | -93 | -143 | 11 | 0 | 4 | 15 | 0 | 0 | 1 | 1069 | 1097 | 1021 | 250 | -88 | -6 | -39 | -6 | -4 | -2 | 52 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1125 | Offshore Wind Connection Occitanie | TOOT | 47 | 49 | 46 | 9 | 11 | 6 | 59 | 62 | 56 | -122 | -88 | -153 | 0 | 0 | 4 | 15 | 0 | 0 | 0 | 1060 | 1074 | 1042 | 250 | -119 | -12 | -26 | -9 | -6 | -4 | -29 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1126 | Offshore Wind Connection PACA | TOOT | 44 | 47 | 42 | 10 | 11 | 9 | 58 | 60 | 57 | -139 | -123 | -157 | -13 | 0 | 4 | 17 | 0 | 0 | -2 | 1039 | 1044 | 1030 | 250 | -109 | -11 | -34 | -6 | -4 | -3 | -98 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1127 | Offshore Wind Connection South Atlantic | PINT | 189 | 196 | 184 | 39 | 43 | 35 | 267 | 276 | 259 | -551 | -505 | -615 | 94 | 0 | 17 | 66 | 0 | 3 | 11 | 4600 | 4607 | 4592 | 1250 | -544 | -50 | -183 | -41 | -27 | -15 | 387 | 18 | N/A | N/A | N/A | N/A | N/A | N/A
1129 | New RES at Minho region | TOOT | 44 | 46 | 41 | 8 | 9 | 8 | 48 | 51 | 45 | -120 | -110 | -128 | 14 | 0 | 4 | 14 | 0 | 0 | 2 | 859 | 877 | 825 | 400 | -68 | -8 | -8 | -4 | -2 | -2 | 55 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
1001st | Kaunertal Extension Project | PINT | 36 | 38 | 34 | 10 | 11 | 8 | 20 | 22 | 18 | -143 | -110 | -164 | -22 | 0 | 4 | 17 | 0 | -1 | -3 | 354 | 384 | 323 | 0 | -171 | -17 | -65 | -13 | -9 | -5 | -34 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
1003st | Hydro pump storage in Bulgaria - Yadenitsa | PINT | 8 | 13 | 3 | 4 | 8 | 0 | 1 | 2 | 0 | -50 | 5 | -118 | -1212 | 0 | 2 | 6 | 0 | -36 | -144 | 15 | 29 | 6 | 0 | -9 | -4 | 18 | -2 | -2 | -1 | -1100 | -165 | N/A | N/A | N/A | N/A | N/A | N/A
1004st | Estonian Pumped-Hydro Energy Storage (please note the name of the Project has been changed due to location change) | PINT | 14 | 22 | 7 | 3 | 6 | 1 | 5 | 5 | 4 | -47 | -17 | -81 | -3 | 0 | 1 | 6 |  | 0 |  | 83 | 94 | 70 | 0 | -50 | -3 | -309 | -5 | -12 | -1 | -87 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1006st | HPS AMFILOCHIA | PINT | 4 | 6 | 2 | 1 | 2 | 0 | 1 | 1 | 1 | -21 | -7 | -30 | -1210 | 0 | 1 | 2 | 0 | -36 | -144 | 21 | 24 | 18 | 0 | 25 | -2 | 59 | 2 | 1 | -1 | -1098 | -165 | N/A | N/A | N/A | N/A | N/A | N/A
1012st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | TOOT | 17 | 24 | 7 | 6 | 9 | 3 | 19 | 21 | 15 | -81 | -41 | -131 | 13 | 0 | 2 | 10 | 0 | 0 | 2 | 335 | 368 | 280 | 0 | 113 | 7 | 62 | 8 | 5 | 2 | 41 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1013st | CAES Zuidwending, NL | PINT | 1 | 1 | 1 | -1879 | 6 | -3763 | 2 | 4 | 0 | 26838 | 53759 | -82 | 716 | 0 | 0 | 0 | 0 | 21 | 85 | 31 | 61 | 0 | 0 | -89 | -7 | -45 | -7 | -4 | -2 | 1976 | 115 | N/A | N/A | N/A | N/A | N/A | N/A
1025st | Silvermines Hydroelectric Power Station | PINT | 20 | 33 | 11 | 3 | 3 | 2 | 14 | 22 | 7 | -43 | -31 | -49 | 2 | 0 | 1 | 5 | 0 | 0 | 0 | 258 | 405 | 128 | 0 | -40 | -9 | 42 | -5 | -4 | -2 | 27 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1026st | Hydro pumped storage Riedl | PINT | 14 | 18 | 7 | 5 | 10 | 3 | 6 | 8 | 4 | -72 | -37 | -139 | 8 | 0 | 2 | 9 | 0 | 0 | 1 | 100 | 146 | 61 | 0 | -101 | -7 | -58 | -8 | -5 | -2 | 86 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1027st | P-PHES CUA | PINT | 22 | 33 | 14 | 6 | 7 | 4 | 12 | 12 | 11 | -82 | -52 | -107 | 21 | 0 | 2 | 10 | 0 | 1 | 2 | 209 | 214 | 207 | 0 | -87 | -11 | -4 | -8 | -6 | -3 | 33 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
1035st | Ptolemaida Battery Energy Storage System | PINT | 7 | 10 | 6 | 0 | 1 | -2 | 0 | 1 | 0 | 3 | 28 | -14 | -1210 | 0 | 0 | 0 | 0 | -36 | -144 | 9 | 12 | 3 | 0 | -23 | -2 | -7 | -3 | -3 | -1 | -1103 | -165 | N/A | N/A | N/A | N/A | N/A | N/A
1036st | SR Mar de Aragon | PINT | 31 | 31 | 31 | 8 | 8 | 8 | 12 | 12 | 12 | -119 | -119 | -119 | N/A | 0 | 4 | 14 | N/A | N/A | N/A | 212 | 212 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1037st | ELSEA - European Large Scale Energy Accumulation | PINT | 8 | 10 | 3 | 1 | 1 | 1 | 1 | 2 | 0 | -11 | -7 | -15 | 3 | 0 | 0 | 1 | 0 | 0 | 0 | 18 | 31 | 0 | 0 | -47 | -3 | -24 | -4 | -3 | -1 | -4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1038st | CAES Zuidwending Extension | PINT | 2 | 2 | 2 | 3 | 7 | -1 | 2 | 4 | 0 | -44 | 10 | -98 | 701 | 0 | 1 | 5 | 0 | 21 | 83 | 38 | 75 | 1 | 0 | -97 | -7 | -35 | -8 | -5 | -2 | 1957 | 113 | N/A | N/A | N/A | N/A | N/A | N/A
1039st | Reversible Hydraulic Power Plant Los Guajares | TOOT | 17 | 21 | 14 | 3 | 6 | 1 | 9 | 10 | 8 | -50 | -18 | -86 | -14 | 0 | 1 | 6 | 0 | 0 | -2 | 166 | 179 | 153 | 0 | -20 | -6 | 30 | -2 | -1 | -2 | -58 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1041st | Purifying – Pumped Hydroelectric Energy Storage “Velilla del Río Carrión” (P-PHES VELILLA) | PINT | 9 | 10 | 9 | 3 | 5 | 1 | 5 | 6 | 4 | -39 | -13 | -69 | 6 | 0 | 1 | 5 | 0 | 0 | 1 | 84 | 99 | 71 | 0 | -35 | -4 | -8 | -3 | -2 | -1 | 10 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1044st | Green Hydrogen Hub CAES | PINT | 1 | 1 | 1 | 5 | 6 | 4 | 3 | 4 | 1 | -71 | -56 | -85 | 4 | 0 | 2 | 8 | 0 | 0 | 1 | 45 | 76 | 14 | 0 | -105 | -6 | -92 | -8 | -6 | -2 | 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1046st | Online Grid Controller “PSKW-Rio” | PINT | 14 | 20 | 7 | 4 | 8 | 1 | 6 | 8 | 4 | -62 | -14 | -110 | -23 | 0 | 2 | 7 | 0 | -1 | -3 | 112 | 140 | 60 | 0 | -107 | -9 | -49 | -7 | -5 | -3 | -68 | -5 | N/A | N/A | N/A | N/A | N/A | N/A
1048st | WSK PULS (PHES) | PINT | 18 | 31 | 8 | 6 | 8 | 3 | 6 | 8 | 4 | -81 | -48 | -118 | -11 | 0 | 2 | 10 | 0 | 0 | -1 | 113 | 153 | 64 | 0 | -102 | -11 | -50 | -6 | -4 | -3 | -30 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1050st | SE Integrator | PINT | 15 | 27 | 8 | 6 | 9 | 3 | 1 | 2 | 1 | -90 | -48 | -132 | 13 | 0 | 3 | 11 | 0 | 0 | 1 | 24 | 34 | 16 | 0 | -108 | -12 | -25 | -8 | -6 | -4 | 31 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1052st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES BUSEIRO) | PINT | 14 | 15 | 14 | 5 | 5 | 4 | 5 | 6 | 4 | -65 | -50 | -78 | 14 | 0 | 2 | 8 | 0 | 0 | 2 | 96 | 119 | 69 | 0 | -55 | -7 | 8 | -5 | -4 | -2 | 25 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 36 | 38 | 35 | 13 | 16 | 9 | 30 | 34 | 26 | -185 | -134 | -226 | 46 | 0 | 6 | 22 | 0 | 1 | 5 | 537 | 592 | 485 | 0 | -133 | -18 | 33 | -12 | -8 | -5 | 98 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
1055st | CAES Leer, Germany | PINT | 1 | 2 | 0 | 4 | 8 | -1 | 4 | 5 | 4 | -53 | 8 | -114 | 5 | 0 | 2 | 6 | 0 | 0 | 1 | 75 | 87 | 64 | 0 | -142 | -7 | -123 | -10 | -7 | -2 | 9 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1056st | CAES Etzel, Germany | PINT | 1 | 1 | 0 | 4 | 8 | -1 | 5 | 5 | 4 | -52 | 8 | -112 | 5 | 0 | 2 | 6 | 0 | 0 | 1 | 78 | 87 | 69 | 0 | -126 | -8 | -86 | -9 | -6 | -2 | 11 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1057st | CAES Harsefeld-Stade, Germany | PINT | 0 | 1 | 0 | 4 | 8 | -1 | 5 | 5 | 4 | -51 | 8 | -110 | 5 | 0 | 2 | 6 | 0 | 0 | 1 | 78 | 87 | 70 | 0 | -136 | -7 | -112 | -10 | -6 | -2 | 10 | 1 | N/A | N/A | N/A | N/A | N/A | N/A

## DE2030_EU
Scenario | DE2030
[16 empty] | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 58 | 66 | 50 | 24 | 27 | 18 | 67 | 76 | 59 | -307 | -234 | -340 | 10 | 0 | 7 | 34 | 0 | 0 | 1 | 1041 | 1374 | 737 | 1154 | -205 | -26 | 10 | -16 | -10 | -8 | 12 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
4 | Interconnection Portugal-Spain | TOOT | 18 | 28 | 8 | 6 | 9 | 4 | 18 | 26 | 13 | -73 | -51 | -110 | 3 | 0 | 2 | 8 | 0 | 0 | 0 | 306 | 468 | 209 | 0 | -220 | -26 | 4 | -18 | -11 | -8 | 0 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
16 | Biscay Gulf | TOOT | 357 | 381 | 330 | 107 | 118 | 92 | 295 | 296 | 295 | -1368 | -1175 | -1508 | 376 | 0 | 30 | 152 | 0 | 8 | 42 | 5274 | 5330 | 5219 | 0 | -1245 | -126 | -247 | -101 | -77 | -38 | 1717 | 70 | N/A | N/A | N/A | N/A | N/A | N/A
26 | Reschenpass Interconnector Project | TOOT | 24 | 30 | 19 | 15 | 17 | 14 | 4 | 6 | 2 | -198 | -175 | -217 | 15 | 0 | 4 | 22 | 0 | 0 | 2 | 66 | 98 | 35 | 0 | -215 | -13 | -103 | -19 | -13 | -4 | 66 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
28 | Italy-Montenegro | PINT | 6 | 9 | 3 | 10 | 10 | 10 | 24 | 25 | 23 | -126 | -122 | -129 | 6 | 0 | 3 | 14 | 0 | 0 | 1 | 391 | 408 | 374 | 0 | -143 | -12 | -57 | -11 | -7 | -4 | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
29 | Italy-Tunisia | TOOT | 50 | 60 | 40 | -61 | -58 | -63 | 59 | 64 | 54 | 778 | 806 | 749 | 25 | 0 | 0 | 0 | 0 | 1 | 3 | 965 | 981 | 949 | 0 | 767 | 88 | 33 | 61 | 39 | 27 | -12 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
33 | Central Northern Italy | TOOT | 20 | 23 | 17 | 13 | 15 | 11 | 20 | 23 | 17 | -165 | -138 | -192 | 21 | 0 | 4 | 18 | 0 | 0 | 2 | 323 | 353 | 294 | 0 | -216 | -12 | -106 | -17 | -10 | -3 | 54 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
35 | CZ Southwest-east corridor | PINT | 40 | 47 | 35 | 5 | 8 | 2 | 7 | 9 | 6 | -69 | -22 | -107 | 68 | 0 | 2 | 8 | 0 | 1 | 8 | 123 | 136 | 111 | 0 | 98 | -11 | 122 | 11 | -5 | -4 | 313 | 12 | N/A | N/A | N/A | N/A | N/A | N/A
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 30 | 34 | 28 | 14 | 18 | 7 | 6 | 7 | 5 | -174 | -84 | -231 | N/A | 0 | 4 | 19 | N/A | N/A | N/A | 92 | 100 | 81 | 0 | -244 | -12 | -158 | -22 | -16 | -3 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 52 | 55 | 51 | 23 | 27 | 20 | 5 | 10 | 2 | -294 | -260 | -343 | 55 | 0 | 6 | 33 | 0 | 1 | 6 | 89 | 180 | 43 | 0 | -369 | -11 | -396 | -28 | -33 | -3 | 292 | 10 | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 18 | 18 | 18 | -18 | -18 | -18 | 11 | 11 | 11 | 233 | 233 | 233 | 19 | 4 | 0 | 0 | 0 | 0 | 2 | 189 | 189 | 189 | 0 | 231 | 23 | 51 | 18 | 11 | 7 | 104 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
85 | Integration of RES in Alentejo | TOOT | 12 | 18 | 8 | 3 | 5 | 2 | 22 | 28 | 16 | -44 | -27 | -62 | 19 | 0 | 1 | 5 | 0 | 0 | 2 | 381 | 503 | 294 | 700 | -39 | -6 | 20 | -4 | -2 | -2 | 218 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
94 | GerPol Improvements | TOOT | 200 | 221 | 183 | 117 | 125 | 112 | 52 | 60 | 48 | -1498 | -1434 | -1601 |  | 0 | 33 | 166 | N/A | N/A | N/A | 884 | 919 | 841 | 0 | -2062 | -24 | -2212 | -187 | -190 | -5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
103 | Reinforcements Ring NL phase I | TOOT | 27 | 29 | 25 | 12 | 16 | 7 | 10 | 10 | 10 | -160 | -84 | -206 | -12 | 0 | 4 | 18 | 0 | 0 | -1 | 167 | 174 | 156 | 0 | -111 | -19 | 125 | -16 | -11 | -5 | -85 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
107 | Celtic Interconnector | TOOT | 135 | 185 | 82 | 29 | 31 | 28 | 104 | 105 | 104 | -374 | -359 | -396 | 177 | 0 | 8 | 42 | 0 | 4 | 20 | 1868 | 1895 | 1833 | 0 | -483 | -50 | -78 | -39 | -28 | -15 | 718 | 31 | N/A | N/A | N/A | N/A | N/A | N/A
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 75 | 76 | 74 | 8 | 10 | 6 | 75 | 77 | 74 | -106 | -82 | -131 | 39 | 0 | 2 | 12 | 0 | 1 | 4 | 1317 | 1330 | 1305 | 0 | -347 | -12 | -650 | -16 | -18 | -4 | 146 | 6 | N/A | N/A | N/A | N/A | N/A | N/A
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 752 | 754 | 750 | 196 | 199 | 190 | 834 | 857 | 811 | -2510 | -2439 | -2555 | 239 | 0 | 55 | 279 | 0 | 5 | 27 | 14690 | 14770 | 14598 | 3500 | -3694 | -275 | -2245 | -241 | -168 | -85 | 798 | 42 | N/A | N/A | N/A | N/A | N/A | N/A
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 17 | 17 | 17 | -48 | -48 | -48 | 7 | 7 | 7 | 613 | 613 | 613 | 130 | 11 | 0 | 0 | 0 | 3 | 12 | 124 | 124 | 124 | 0 | -697 | -60 | -390 | -46 | -46 | -19 | 351 | 19 | N/A | N/A | N/A | N/A | N/A | N/A
123 | LitPol Link Stage 2 | TOOT | 189 | 191 | 186 | 163 | 164 | 162 | 46 | 47 | 45 | -2089 | -2077 | -2101 | -22 | 0 | 46 | 232 | N/A | 0 | N/A | 807 | 816 | 797 | 0 | -2849 | -23 | -3043 | -216 | -185 | -5 | -36 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
124 | NordBalt phase 2 | PINT | 45 | 57 | 36 | 10 | 11 | 10 | 24 | 27 | 21 | -132 | -124 | -141 | -28 | 0 | 3 | 15 | N/A | -1 | N/A | 404 | 431 | 364 | 0 | -135 | -10 | -133 | -10 | -9 | -3 | -120 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
126 | SE North-south short-term reinforcements | TOOT | 133 | 161 | 109 | 26 | 32 | 23 | 26 | 28 | 23 | -337 | -295 | -412 | 41 | 0 | 7 | 37 | 0 | 1 | 5 | 447 | 478 | 416 | 0 | -299 | -31 | -180 | -27 | -26 | -9 | 100 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
127 | Central Southern Italy | TOOT | 30 | 40 | 23 | 10 | 11 | 10 | 47 | 50 | 42 | -132 | -128 | -139 | 26 | 0 | 3 | 15 | 0 | 1 | 3 | 789 | 852 | 754 | 0 | -157 | -19 | 1 | -13 | -8 | -6 | 126 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2008 | 2008 | 2008 | 52 | 52 | 52 | 343 | 343 | 343 | -1858 | -1858 | -1858 | 299 | 0 | 41 | 206 | 0 | -7 | -33 | 3426 | 3426 | 3426 | 0 | -2937 | -2937 | -4085 | -166 | -265 | -25 | 1334 | -49 | N/A | N/A | N/A | N/A | N/A | N/A
132 | HVDC Line A-North | TOOT | 5283 | 5283 | 5283 | 129 | 129 | 129 | 896 | 896 | 896 | -4605 | -4605 | -4605 | 718 | 0 | 101 | 511 | 0 | -16 | -80 | 8961 | 8961 | 8961 | 0 | -6860 | -6860 | -7266 | -475 | -496 | -71 | 3004 | -119 | N/A | N/A | N/A | N/A | N/A | N/A
138 | Black Sea Corridor | TOOT | 48 | 49 | 46 | 20 | 24 | 17 | 18 | 24 | 14 | -255 | -216 | -304 | N/A | 0 | 6 | 28 | N/A | N/A | N/A | 311 | 360 | 256 | 0 | -248 | -34 | 67 | -22 | -13 | -10 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
142 | CSE4 | TOOT | 10 | 14 | 8 | 5 | 7 | 3 | 10 | 14 | 7 | -59 | -34 | -89 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 162 | 210 | 116 | 0 | -33 | -7 | 40 | -4 | -2 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
144 | Mid Continental East corridor | TOOT | 77 | 82 | 72 | 45 | 51 | 40 | 57 | 68 | 49 | -574 | -511 | -659 | -101 | 0 | 13 | 64 | 0 | -2 | -11 | 967 | 1034 | 869 | 0 | -679 | -57 | -235 | -55 | -35 | -17 | -454 | -17 | N/A | N/A | N/A | N/A | N/A | N/A
150 | Italy-Slovenia | light PINT | 57 | 60 | 52 | 27 | 30 | 25 | 10 | 15 | 5 | -351 | -319 | -386 | 61 | 0 | 8 | 39 | 0 | 1 | 7 | 174 | 275 | 72 | 0 | -242 | -32 | 58 | -22 | -11 | -9 | 202 | 11 | N/A | N/A | N/A | N/A | N/A | N/A
153 | France-Alderney-Britain | PINT | 84 | 84 | 84 | -29 | -29 | -29 | 19 | 19 | 19 | 370 | 370 | 370 | 176 | 7 | 0 | 0 | 0 | 4 | 20 | 342 | 342 | 342 | 0 | 90 | 52 | -529 | 17 | 3 | 15 | 700 | 31 | N/A | N/A | N/A | N/A | N/A | N/A
170 | Baltic States Synchronization with Continental Europe | TOOT | 255 | 276 | 239 | 227 | 236 | 217 | 66 | 69 | 63 | -2916 | -2778 | -3021 | -4 | 0 | 64 | 324 | N/A | 0 | N/A | 1284 | 1480 | 1125 | 0 | -3842 | -34 | -4086 | -291 | -255 | -8 | 97 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
174 | Greenconnector | PINT | 31 | 41 | 18 | 35 | 38 | 29 | 6 | 7 | 5 | -450 | -370 | -493 | 57 | 0 | 10 | 50 | 0 | 1 | 6 | 102 | 118 | 71 | 0 | -514 | -43 | -186 | -41 | -27 | -13 | 129 | 9 | N/A | N/A | N/A | N/A | N/A | N/A
176 | Hansa PowerBridge I | TOOT | 223 | 225 | 221 | 109 | 111 | 107 | 52 | 57 | 48 | -1402 | -1376 | -1427 | N/A | 0 | 31 | 156 | N/A | N/A | N/A | 915 | 982 | 847 | 0 | -1757 | -118 | -985 | -134 | -103 | -35 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
183 | DKW-DE, Westcoast | TOOT | 193 | 202 | 182 | 87 | 95 | 80 | 112 | 116 | 104 | -1120 | -1023 | -1224 | N/A | 0 | 25 | 124 | N/A | N/A | N/A | 2024 | 2166 | 1839 | 0 | -1116 | -106 | -148 | -103 | -73 | -31 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
186 | East of Austria | TOOT | 308 | 310 | 306 | 93 | 95 | 91 | 324 | 324 | 323 | -1191 | -1167 | -1215 | -9 | 0 | 26 | 132 | 0 | 0 | -1 | 5858 | 5864 | 5851 | 2000 | -1457 | -127 | -525 | -112 | -72 | -38 | -47 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
187 | St. Peter (AT) - Pleinting (DE) | PINT | 139 | 155 | 119 | 51 | 53 | 48 | 11 | 14 | 8 | -648 | -615 | -680 | 144 | 0 | 14 | 72 | 0 | 3 | 16 | 184 | 215 | 130 | 0 | -976 | -28 | -1086 | -70 | -84 | -9 | 711 | 25 | N/A | N/A | N/A | N/A | N/A | N/A
190 | NorthConnect | TOOT | 0 | 0 | 0 | 58 | 58 | 58 | 25 | 25 | 25 | -740 | -740 | -740 | 4 | 0 | 16 | 82 | 0 | 0 | 0 | 454 | 454 | 454 | 0 | -450 | -69 | 366 | -57 | -46 | -19 | 61 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 47 | 57 | 35 | 11 | 13 | 10 | 9 | 14 | 7 | -142 | -124 | -164 | 51 | 0 | 3 | 16 | 0 | 1 | 6 | 150 | 210 | 121 | 0 | -249 | -12 | -251 | -16 | -22 | -4 | 250 | 9 | N/A | N/A | N/A | N/A | N/A | N/A
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 10 | 15 | 3 | 9 | 10 | 8 | 2 | 6 | 0 | -110 | -99 | -125 | 3 | 0 | 2 | 12 | 0 | 0 | 0 | 42 | 104 | 1 | 0 | -129 | -11 | -42 | -10 | -7 | 3 | 6 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
219 | EuroAsia Interconnector | TOOT | 530 | 644 | 416 | 13 | 29 | -3 | 320 | 349 | 291 | -162 | 44 | -368 | 210 | 0 | 4 | 18 | 0 | 5 | 23 | 5226 | 5305 | 5147 | 0 | 16 | 7 | -83 | 1 | -2 | 2 | 708 | 34 | N/A | N/A | N/A | N/A | N/A | N/A
225 | 2nd interconnector Belgium - Germany | light PINT | 53 | 63 | 42 | 28 | 31 | 24 | 12 | 13 | 10 | -363 | -313 | -403 |  | 0 | 8 | 40 | N/A | N/A | N/A | 210 | 242 | 175 | 0 | -447 | -26 | -242 | -40 | -30 | -7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
227 | Transbalkan Corridor | TOOT | -2 | 2 | 0 | 10 | 13 | 7 | 9 | 15 | 6 | -127 | -95 | -168 | 4 | 0 | 3 | 14 | 0 | 0 | 0 | 151 | 231 | 109 | 0 | -157 | -21 | 30 | -13 | -8 | -6 | 8 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
228 | Muhlbach - Eichstetten | TOOT | 53 | 58 | 49 | 21 | 23 | 20 | 5 | 6 | 4 | -271 | -254 | -296 | 35 | 0 | 6 | 30 | 0 | 1 | 4 | 86 | 96 | 68 | 0 | -393 | -14 | -363 | -29 | -24 | -4 | 183 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
230 | GerPol Power Bridge I | TOOT | 349 | 372 | 318 | 337 | 339 | 335 | 27 | 33 | 22 | -4319 | -4291 | -4348 | N/A | 0 | 95 | 479 | N/A | N/A | N/A | 441 | 495 | 394 | 0 | -6821 | 52 | -10135 | -473 | -537 | 15 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
231 | Beznau - Tiengen | PINT | 12 | 14 | 6 | 13 | 19 | 7 | 7 | 8 | 5 | -169 | -94 | -237 | N/A | 0 | 4 | 19 | N/A | N/A | N/A | 120 | 139 | 93 | 0 | -208 | -20 | -23 | -20 | -16 | -6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9782 | 9782 | 9782 | 238 | 238 | 238 | 1689 | 1689 | 1689 | -8496 | -8496 | -8496 | 1065 | 0 | 187 | 943 | 0 | -23 | -118 | 16890 | 16890 | 16890 | 0 | -12217 | -12217 | -12224 | -855 | -867 | -143 | 4053 | -176 | N/A | N/A | N/A | N/A | N/A | N/A
239 | Fenno-Skan 1 renewal | light PINT | 32 | 36 | 29 | 4 | 6 | 2 | 34 | 40 | 30 | -48 | -26 | -81 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 566 | 610 | 514 | 0 | -127 | -1 | -249 | -5 | -6 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 7 | 15 | 3 | 2 | 4 | -1 | 2 | 2 | 1 | -23 | 17 | -54 | N/A | 0 | 0 | 3 | N/A | N/A | N/A | 29 | 44 | 21 | 0 | -25 | -5 | 27 | -3 | -2 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
244 | Vigy - Uchtelfangen area | PINT | 246 | 284 | 213 | 94 | 102 | 87 | 24 | 27 | 20 | -1208 | -1110 | -1306 | 216 | 0 | 27 | 134 | 0 | 5 | 24 | 403 | 497 | 302 | 0 | -2253 | -83 | -2165 | -158 | -132 | -25 | 1053 | 40 | N/A | N/A | N/A | N/A | N/A | N/A
245 | Upgrade Meeden - Diele | TOOT | 17 | 23 | 11 | 7 | 8 | 7 | 3 | 4 | 2 | -93 | -83 | -103 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 50 | 68 | 31 | 0 | 33 | 9 | -81 | 6 | 4 | 2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
247 | AQUIND Interconnector | PINT | 111 | 111 | 111 | -41 | -41 | -41 | 27 | 27 | 27 | 525 | 525 | 525 | 198 | 9 | 0 | 0 | 0 | 4 | 22 | 468 | 468 | 468 | 0 | 161 | 79 | -748 | 25 | 4 | 23 | 745 | 35 | N/A | N/A | N/A | N/A | N/A | N/A
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 11 | 18 | 6 | 6 | 8 | 2 | 3 | 8 | 1 | -81 | -30 | -108 | -3 | 0 | 2 | 9 | 0 | 0 | 0 | 51 | 141 | 11 | 0 | -104 | -6 | -72 | -8 | -5 | -2 | -4 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | [6 empty] | -35 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 14 | 35 | 0 | 10 | 14 | 8 | 1 | 2 | 1 | -132 | -107 | -174 | 148 | 0 | 3 | 15 | 0 | 3 | 16 | 25 | 41 | 12 | 0 | -167 | -13 | -127 | -10 | -12 | -4 | 752 | 28 | N/A | N/A | N/A | N/A | N/A | N/A
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 447 | 447 | 447 | 12 | 12 | 12 | 47 | 47 | 47 | -411 | -411 | -411 | 193 | 0 | 14 | 50 | 0 | -4 | -21 | 465 | 465 | 465 | 0 | -626 | -626 | -1053 | -36 | -57 | 1 | 546 | -33 | N/A | N/A | N/A | N/A | N/A | N/A
259 | HU-RO | PINT | 56 | 61 | 48 | 19 | 21 | 18 | 24 | 29 | 21 | -245 | -227 | -274 | 76 | 0 | 5 | 27 | 0 | 2 | 8 | 403 | 442 | 371 | 0 | -170 | -24 | 5 | -12 | -9 | -7 | 424 | 14 | N/A | N/A | N/A | N/A | N/A | N/A
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 0 | 0 | 0 | -45 | -45 | -45 | 18 | 20 | 16 | 579 | 582 | 577 | 164 | 0 | 0 | 0 | 0 | 4 | 18 | 296 | 351 | 241 | 2000 | -1083 | -75 | -894 | -58 | -56 | -24 | 466 | 28 | N/A | N/A | N/A | N/A | N/A | N/A
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 36 | 51 | 20 | 17 | 19 | 14 | 22 | 28 | 18 | -212 | -183 | -244 | N/A | 0 | 5 | 24 | N/A | N/A | N/A | 366 | 429 | 324 | 0 | 170 | 15 | -21 | 21 | 15 | 4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
263 | Lake Constance East | light PINT | 134 | 146 | 122 | 60 | 61 | 58 | 10 | 13 | 8 | -766 | -749 | -780 | N/A | 0 | 17 | 85 | N/A | N/A | N/A | 171 | 196 | 146 | 0 | -1390 | -18 | -1678 | -103 | -106 | -5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
267 | Hansa PowerBridge II | light PINT | 199 | 199 | 199 | 101 | 103 | 99 | 46 | 50 | 43 | -1295 | -1269 | -1321 | N/A | 0 | 28 | 144 | N/A | N/A | N/A | 803 | 851 | 754 | 0 | -1714 | -112 | -965 | -128 | -95 | -33 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 187 | 191 | 184 | 55 | 64 | 47 | 173 | 177 | 170 | -700 | -599 | -817 | 372 | 0 | 15 | 78 | 0 | 8 | 41 | 3095 | 3190 | 3000 | 0 | -723 | -69 | -222 | -56 | -46 | -21 | 1511 | 68 | N/A | N/A | N/A | N/A | N/A | N/A
276 | FR-ES project -Navarra-Landes | PINT | 187 | 191 | 184 | 55 | 64 | 47 | 173 | 177 | 170 | -700 | -599 | -817 | 368 | 0 | 15 | 78 | 0 | 8 | 41 | 3095 | 3190 | 3000 | 0 | -723 | -69 | -222 | -56 | -46 | -21 | 1511 | 68 | N/A | N/A | N/A | N/A | N/A | N/A
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 117 | 118 | 116 | 44 | 48 | 40 | 3 | 3 | 2 | -561 | -509 | -613 | 96 | 0 | 12 | 62 | 0 | 2 | 11 | 45 | 56 | 35 | 0 | -1197 | -37 | -1378 | -69 | -63 | -12 | 444 | 18 | N/A | N/A | N/A | N/A | N/A | N/A
283 | TuNur Italy | PINT | 10 | 10 | 10 | 191 | 201 | 181 | 0 | 0 | 0 | -2446 | -2318 | -2575 | -85 | 0 | 54 | 272 | 0 | -2 | -9 | 0 | 0 | 0 | 4900 | -2503 | -290 | -111 | -199 | -127 | -87 | -342 | -15 | N/A | N/A | N/A | N/A | N/A | N/A
285 | GridLink | PINT | 84 | 84 | 84 | -29 | -29 | -29 | 19 | 19 | 19 | 370 | 370 | 370 | 201 | 7 | 0 | 0 | 0 | 4 | 22 | 342 | 342 | 342 | 0 | 75 | 52 | -552 | 16 | 3 | 15 | 787 | 36 | N/A | N/A | N/A | N/A | N/A | N/A
286 | Greenlink | TOOT | 20 | 20 | 20 | 2 | 2 | 2 | 73 | 73 | 73 | -31 | -31 | -31 | 23 | 0 | 1 | 3 | 0 | 1 | 3 | 1299 | 1299 | 1299 | 0 | -68 | 5 | -141 | -5 | -4 | 2 | 118 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
293 | Southern Aegean Interconnector | PINT | 59 | 65 | 54 | 20 | 21 | 18 | 66 | 70 | 65 | -255 | -234 | -275 | 86 | 0 | 6 | 28 | 0 | 2 | 10 | 1115 | 1172 | 1058 | 582 | -336 | -23 | -179 | -27 | -18 | -7 | 201 | 16 | N/A | N/A | N/A | N/A | N/A | N/A
297 | BRABO II + III | TOOT | 36 | 51 | 20 | 17 | 19 | 14 | 22 | 28 | 18 | -212 | -183 | -244 | 103 | 0 | 5 | 24 | 0 | 2 | 11 | 366 | 429 | 324 | 0 | -170 | -15 | 21 | -21 | -15 | -4 | 371 | 18 | N/A | N/A | N/A | N/A | N/A | N/A
299 | SACOI3 | TOOT | 79 | 90 | 66 | 32 | 37 | 27 | 57 | 65 | 49 | -413 | -348 | -472 | 26 | 0 | 9 | 46 | 0 | 1 | 3 | 968 | 1030 | 880 | 0 | -445 | -53 | 3 | -36 | -23 | -16 | 113 | 5 | N/A | N/A | N/A | N/A | N/A | N/A
309 | NeuConnect | TOOT | 41 | 41 | 41 | -13 | -13 | -13 | 18 | 18 | 18 | 167 | 167 | 167 | 184 | 3 | 0 | 0 | 0 | 4 | 20 | 327 | 327 | 327 | 0 | 117 | 11 | 141 | 3 | 14 | 4 | 539 | 30 | N/A | N/A | N/A | N/A | N/A | N/A
312 | St. Peter (AT) - Tauern (AT) | TOOT | 224 | 229 | 220 | 87 | 94 | 81 | 25 | 30 | 19 | -1119 | -1037 | -1200 | 160 | 0 | 25 | 124 | 0 | 4 | 18 | 420 | 467 | 340 | 0 | -1861 | -23 | -2422 | -129 | -149 | -7 | 893 | 29 | N/A | N/A | N/A | N/A | N/A | N/A
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 219 | 229 | 203 | 95 | 110 | 81 | 23 | 30 | 18 | -1219 | -1037 | -1409 | 187 | 0 | 27 | 135 | 0 | 4 | 21 | 393 | 467 | 312 | 0 | -1861 | -23 | -2422 | -129 | -149 | -7 | 977 | 34 | N/A | N/A | N/A | N/A | N/A | N/A
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 3 | 4 | 1 | 1 | 3 | -1 | 2 | 3 | 1 | -15 | 19 | -43 | -4 | 0 | 0 | 2 | 0 | 0 | 0 | 32 | 58 | 17 | 0 | -62 | -6 | -10 | -5 | -3 | -2 | -10 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 2 | 3 | 2 | 3 | 5 | 2 | 3 | 3 | 2 | -43 | -29 | -64 | -4 | 0 | 1 | 5 | 0 | 0 | 0 | 45 | 53 | 30 | 0 | -15 | -3 | 15 | -2 | -1 | -1 | -15 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
325 | Obersielach (AT) - Podlog (SI) | PINT | 16 | 25 | 8 | 12 | 17 | 7 | 4 | 6 | 4 | -155 | -88 | -223 | 46 | 0 | 3 | 17 | 0 | 1 | 5 | 73 | 112 | 59 | 0 | -200 | -17 | -52 | -16 | -6 | -5 | 146 | 8 | N/A | N/A | N/A | N/A | N/A | N/A
328 | Interconnector DE-LUX | TOOT | 4 | 7 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | -20 | -14 | -28 |  | 0 | 0 | 2 | N/A | N/A | N/A | 22 | 39 | 12 | 0 | 10 | -4 | 63 | 0 | 1 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | [6 empty] | 42 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
330 | 4th 400kV CZ-SK interconnector | light PINT | 13 | 20 | 8 | 10 | 12 | 6 | 0 | 1 | 0 | -123 | -74 | -159 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 5 | 11 | 0 | 0 | -302 | -2 | -328 | -25 | -17 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
333 | PST Foretaille | PINT | 56 | 63 | 52 | 50 | 54 | 47 | 7 | 12 | 4 | -643 | -606 | -692 | 123 | 0 | 14 | 71 | 0 | 3 | 14 | 128 | 215 | 63 | 0 | -764 | -73 | -174 | -62 | -40 | -22 | 634 | 23 | N/A | N/A | N/A | N/A | N/A | N/A
335 | Project 335 - North Sea Wind Power Hub | light PINT | 1002 | 1020 | 979 | 839 | 853 | 829 | 3154 | 3263 | 3034 | -10751 | -10630 | -10936 | N/A | 0 | 237 | 1193 | N/A | N/A | N/A | 55621 | 56081 | 54845 | 12000 | -14930 | -1028 | -9170 | -1048 | -736 | -313 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
338 | Adriatic HVDC link | PINT | 55 | 69 | 41 | 29 | 32 | 25 | 40 | 53 | 26 | -366 | -319 | -414 | -7 | 0 | 8 | 41 | 0 | 0 | -1 | 640 | 813 | 467 | 0 | -358 | -38 | -55 | -28 | -18 | -11 | 2 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
339 | Italian HVDC tri-terminal link | PINT | 53 | 54 | 52 | 17 | 23 | 10 | 69 | 73 | 66 | -217 | -134 | -301 | 112 | 0 | 5 | 24 | 0 | 2 | 12 | 1136 | 1165 | 1108 | 0 | -312 | -35 | -27 | -24 | -15 | -11 | -190 | 16 | N/A | N/A | N/A | N/A | N/A | N/A
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -99 | 0 | 0 | 0 | 0 | -2 | -11 | 0 | 0 | 0 | 0 | [6 empty] | -374 | -18 | N/A | N/A | N/A | N/A | N/A | N/A
341 | North CSE Corridor | PINT | 27 | 33 | 21 | 13 | 14 | 12 | 20 | 21 | 19 | -166 | -154 | -178 | N/A | 0 | 4 | 18 | N/A | N/A | N/A | 339 | 379 | 300 | 0 | -207 | -12 | -148 | -14 | -10 | -4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
342 | Central Balkan Corridor | PINT | 13 | 16 | 9 | 10 | 13 | 9 | 6 | 10 | 2 | -130 | -111 | -165 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 103 | 148 | 44 | 0 | -120 | -7 | -85 | -9 | -6 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
343 | CSE1 New | PINT | 5 | 8 | 0 | 3 | 3 | 2 | 2 | 4 | 0 | -33 | -22 | -41 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 25 | 63 | 0 | 0 | -60 | -5 | -25 | -4 | -3 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
344 | Reinforcements Ring NL phase II | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
345 | 3rd circuit Diemen-Lelystad-Ens | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
346 | ZuidWest380 NL Oost | PINT | 23 | 25 | 21 | 7 | 9 | 5 | 16 | 20 | 12 | -90 | -68 | -110 | -239 | 0 | 2 | 10 | 0 | -5 | -27 | 260 | 310 | 208 | 0 | -101 | -7 | -22 | -11 | -7 | -2 | -1723 | -49 | N/A | N/A | N/A | N/A | N/A | N/A
347 | 3rd circuit Krimpen a/d IJssel - Geertruidenberg | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
348 | NoordWest380 NL | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
349 | MaresConnect | TOOT | 36 | 36 | 36 | 1 | 1 | 1 | 103 | 103 | 103 | -9 | -9 | -9 | 66 | 0 | 0 | 1 | 0 | 1 | 7 | 1821 | 1821 | 1821 | 0 | -68 | 5 | -141 | -5 | -4 | 2 | 254 | 11 | N/A | N/A | N/A | N/A | N/A | N/A
350 | South Balkan Corridor | TOOT | 1 | 2 | 0 | 7 | 14 | 4 | 4 | 8 | 2 | -90 | -50 | -174 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 65 | 127 | 38 | 0 | -61 | -6 | 1 | -6 | -4 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 41 | 49 | 34 | 24 | 28 | 17 | 8 | 15 | 2 | -303 | -212 | -364 | 28 | 0 | 7 | 34 | 0 | 1 | 3 | 134 | 270 | 41 | 0 | -503 | -35 | -217 | -42 | -24 | -10 | 116 | 5 | N/A | N/A | N/A | N/A | N/A | N/A
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 1 | 1 | 0 | 0 | 2 | -3 | 1 | 1 | 0 | 4 | 40 | -24 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 10 | 19 | 3 | 0 | -15 | 1 | -30 | -1 | -1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 23 | 25 | 21 | 7 | 10 | 5 | 16 | 20 | 13 | -95 | -68 | -123 | 26 | 0 | 2 | 11 | 0 | 1 | 3 | 270 | 310 | 237 | 0 | -89 | -4 | -33 | -10 | -7 | -1 | 104 | 5 | N/A | N/A | N/A | N/A | N/A | N/A
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | [6 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7182 | 7182 | 7182 | 163 | 163 | 163 | 1202 | 1202 | 1202 | -5819 | -5819 | -5819 | 1115 | 0 | 128 | 646 | 0 | -25 | -124 | 12027 | 12027 | 12027 | 0 | -8131 | -8131 | -6974 | -610 | -517 | -103 | 5510 | -191 | N/A | N/A | N/A | N/A | N/A | N/A
1039 | SE North-south long-term reinforcements | light PINT | 28 | 38 | 20 | 8 | 14 | 1 | 0 | 0 | 0 | -104 | -16 | -178 | N/A | 0 | 2 | 12 | N/A | N/A | N/A | 91 | 259 | 7 | 0 | -260 | -6 | -331 | -17 | -13 | -2 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1040 | LirIC | PINT | 46 | 46 | 46 | 5 | 5 | 5 | 64 | 64 | 64 | -69 | -69 | -69 | -10 | 0 | 2 | 8 | 0 | 0 | -1 | 1141 | 1141 | 1141 | 0 | -152 | 5 | -278 | -8 | -8 | 1 | 153 | -2 | 0 | 0 | 0 | 0 | 0 | 0
1041 | GREGY Green Energy Interconnector | PINT | 170 | 174 | 165 | 12 | 90 | -79 | 67 | 89 | 49 | -155 | 1012 | -1157 | 208 | 0 | 3 | 17 | 0 | 5 | 23 | 1122 | 1352 | 874 | 0 | 1213 | 113 | 332 | 95 | 61 | 34 | 723 | 39 | N/A | N/A | N/A | N/A | N/A | N/A
1042 | Offshore Wind LT 1 | PINT | 58 | 68 | 52 | 5 | 6 | 4 | 100 | 108 | 96 | -67 | -46 | -82 | -6 | 0 | 1 | 7 | N/A | 0 | N/A | 1610 | 1697 | 1519 | 700 | -120 | -5 | -151 | -6 | -4 | -2 | -153 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1046 | Finnish North-South reinforcement | PINT | 113 | 113 | 113 | 22 | 22 | 22 | 235 | 235 | 235 | -278 | -278 | -278 | -62 | 0 | 6 | 31 | 0 | -1 | -7 | 4178 | 4178 | 4178 | 0 | [6 empty] | -624 | -11 | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 54 | 56 | 53 | 18 | 22 | 12 | 13 | 15 | 12 | -226 | -156 | -281 | N/A | 0 | 5 | 25 | N/A | N/A | N/A | 222 | 263 | 198 | 0 | -213 | -19 | -18 | -23 | -19 | -5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 370 | 375 | 363 | 5 | 15 | -9 | 501 | 512 | 492 | -67 | 112 | -192 | 872 | 0 | 1 | 7 | 0 | 19 | 97 | 8978 | 9037 | 8883 | 0 | -174 | -17 | -39 | -13 | -8 | -5 | 2158 | 127 | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 20 | 20 | 20 | -40 | -40 | -40 | 10 | 10 | 10 | 519 | 519 | 519 | 72 | 9 | 0 | 0 | 0 | 2 | 8 | 177 | 177 | 177 | 0 | 503 | 56 | 87 | 41 | 41 | 17 | 265 | 12 | 0 | 0 | 0 | 0 | 0 | 0
1050 | Tarchon Energy Ltd | PINT | 32 | 32 | 32 | -7 | -7 | -7 | 18 | 18 | 18 | 88 | 88 | 88 | 143 | 2 | 0 | 0 | 0 | 3 | 16 | 310 | 310 | 310 | 0 | 97 | 22 | -25 | 5 | 15 | 7 | 430 | 23 | 0 | 0 | 0 | 0 | 0 | 0
1051 | Aminth Energy Ltd | PINT | 117 | 117 | 117 | 6 | 6 | 6 | 108 | 108 | 108 | -75 | -75 | -75 | 41 | 0 | 2 | 8 | 0 | 1 | 5 | 1906 | 1906 | 1906 | 0 | 254 | -4 | 511 | 5 | 14 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0
1052 | Lienz (AT) - Obersielach (AT) | PINT | 13 | 15 | 11 | 11 | 13 | 7 | 5 | 6 | 4 | -135 | -88 | -172 | 38 | 0 | 3 | 15 | 0 | 1 | 4 | 82 | 112 | 59 | 0 | -200 | -17 | -52 | -16 | -6 | -5 | 137 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 51 | 52 | 49 | 23 | 25 | 20 | 6 | 10 | 3 | -289 | -260 | -321 | 72 | 0 | 6 | 32 | 0 | 2 | 8 | 105 | 180 | 60 | 0 | -369 | -11 | -396 | -28 | -33 | -3 | 341 | 13 | N/A | N/A | N/A | N/A | N/A | N/A
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 260 | 266 | 254 | 67 | 80 | 51 | 249 | 252 | 246 | -857 | -660 | -1026 | 99 | 0 | 19 | 95 | 0 | 2 | 11 | 4412 | 4456 | 4338 | 0 | -1114 | -133 | 27 | -92 | -58 | -40 | 373 | 18 | N/A | N/A | N/A | N/A | N/A | N/A
1058 | HVDC Interconnector DE-CH | light PINT | 53 | 75 | 23 | 50 | 55 | 41 | 15 | 22 | 9 | -639 | -527 | -708 | N/A | 0 | 14 | 71 | N/A | N/A | N/A | 251 | 393 | 164 | 0 | -1010 | -18 | -1153 | -76 | -76 | -5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1059 | Southern Italy | PINT | 4 | 5 | 3 | 1 | 1 | 0 | 9 | 11 | 6 | -10 | -1 | -17 | -10 | 0 | 0 | 1 | 0 | 0 | -1 | 147 | 193 | 84 | 0 | 42 | 8 | -55 | 6 | 3 | 2 | -37 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1063 | ZuidWest380 West | PINT | 23 | 25 | 22 | 8 | 10 | 5 | 19 | 20 | 17 | -97 | -68 | -125 |  | 0 | 2 | 11 | N/A | N/A | N/A | 303 | 310 | 295 | 0 | -28 | 3 | -41 | -5 | -4 | 1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1066 | Bulgaria - Turkey | light PINT | 99 | 120 | 80 | -156 | -141 | -167 | 18 | 27 | 9 | 2004 | 2147 | 1801 | -59 | 0 | 0 | 0 | 0 | -1 | -7 | 290 | 410 | 170 | 0 | 2200 | 258 | 27 | 178 | 113 | 77 | 34 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 46 | 55 | 37 | -85 | -77 | -91 | 19 | 25 | 16 | 1085 | 1167 | 990 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 326 | 385 | 282 | 0 | 1250 | 148 | -11 | 102 | 64 | 44 | -239 | -10 | N/A | N/A | N/A | N/A | N/A | N/A
1068 | LaSGo Link | light PINT | 45 | 46 | 43 | 10 | 12 | 8 | 19 | 21 | 18 | -131 | -107 | -149 | -3 | 0 | 3 | 15 | 0 | 0 | 4 | 322 | 341 | 310 | 0 | -115 | 0 | -227 | -6 | -6 | 0 | 34 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1074 | Pannonian Corridor | PINT | 5 | 7 | 2 | 5 | 6 | 4 | 2 | 3 | 1 | -63 | -53 | -71 | -59 | 0 | 1 | 7 | 0 | -1 | -7 | 33 | 45 | 13 | 0 | -1 | 3 | -55 | 2 | 1 | 1 | -239 | -10 | N/A | N/A | N/A | N/A | N/A | N/A
1082 | Sea-Socket | light PINT | 69 | 80 | 58 | 24 | 25 | 23 | 108 | 110 | 107 | -305 | -299 | -318 | -1 | 0 | 7 | 34 | N/A | 0 | N/A | 1926 | 1938 | 1911 | 700 | -366 | -34 | -123 | -27 | -19 | -10 | -11 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1085 | Malta-Italy Cable Link No.2 | PINT | 8 | 10 | 6 | 3 | 4 | 2 | 3 | 4 | 1 | -42 | -29 | -54 | 34 | 0 | 1 | 5 | 0 | 1 | 4 | 42 | 73 | 12 | 0 | 37 | 7 | -53 | 5 | 3 | 2 | 96 | 6 | N/A | N/A | N/A | N/A | N/A | N/A
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 55 | 57 | 54 | 5 | 6 | 4 | 87 | 89 | 85 | -61 | -50 | -81 | -3 | 0 | 1 | 7 | 0 | 0 | 28 | 1453 | 1511 | 1350 | 700 | -49 | 4 | -209 | 1 | -2 | 1 | -11 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1088 | Off-shore Wind Park in Latvia and Estonia - ELWIND | PINT | 3 | 5 | 1 | 6 | 7 | 5 | 152 | 155 | 150 | -79 | -67 | -94 | -1 | 0 | 2 | 9 | 0 | 0 | 28 | 2575 | 2730 | 2416 | 1000 | -83 | 5 | -356 | -1 | -6 | 1 | -77 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1092 | Offshore Hybrid HVDC Interconnector BEDK | PINT | 271 | 274 | 267 | 184 | 190 | 181 | 696 | 717 | 672 | -2364 | -2316 | -2438 | 253 | 0 | 52 | 262 | 0 | 6 | 28 | 12309 | 12430 | 12141 | 3000 | -3409 | -241 | -2112 | -234 | -172 | -74 | 885 | 43 | N/A | N/A | N/A | N/A | N/A | N/A
1094 | Estlink 3 | light PINT | 52 | 62 | 44 | 13 | 15 | 12 | 33 | 41 | 29 | -168 | -151 | -190 | -11 | 0 | 4 | 19 | 0 | 0 | 13 | 552 | 626 | 502 | 0 | -81 | -6 | -247 | -6 | -11 | -2 | -28 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 49 | 49 | 48 | 7 | 8 | 5 | 50 | 51 | 47 | -85 | -61 | -105 | 0 | 0 | 2 | 9 | N/A | 0 | N/A | 833 | 898 | 717 | 0 | -282 | -5 | -493 | -13 | -13 | -2 | 470 | 20 | N/A | N/A | N/A | N/A | N/A | N/A
1096 | Beznau - Mettlen | PINT | 11 | 18 | 5 | 15 | 19 | 7 | 8 | 11 | 5 | -191 | -93 | -239 | 89 | 0 | 4 | 21 | 0 | 2 | 10 | 140 | 185 | 94 | 0 | -97 | -21 | 152 | -13 | -9 | -6 | -84 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1097 | Upgrade to Konti-Skan | PINT | 122 | 131 | 109 | 42 | 48 | 34 | 37 | 40 | 36 | -535 | -432 | -621 | 120 | 0 | 12 | 59 | 0 | 3 | 13 | 633 | 645 | 609 | 0 | -1081 | -46 | -1024 | -68 | -56 | -14 | 470 | 20 | N/A | N/A | N/A | N/A | N/A | N/A
1098 | Offshore Wind LT 2 | PINT | 60 | 68 | 52 | 6 | 6 | 4 | 97 | 107 | 85 | -71 | -56 | -82 | 0 | 0 | 2 | 8 | N/A | 0 | N/A | 1586 | 1697 | 1519 | 700 | -120 | -5 | -151 | -6 | -4 | -2 | -84 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 17 | 18 | 16 | 6 | 8 | 5 | 7 | 8 | 6 | -83 | -59 | -105 | 89 | 0 | 2 | 9 | 0 | 2 | 10 | 124 | 142 | 105 | 0 | -46 | -10 | 69 | -6 | -4 | -3 | 374 | 16 | N/A | N/A | N/A | N/A | N/A | N/A
1102 | Mettlen - Ulrichen | light PINT | 2 | 4 | 1 | 4 | 5 | 2 | 1 | 2 | 1 | -51 | -26 | -67 | 18 | 0 | 1 | 6 | 0 | 0 | 2 | 23 | 35 | 12 | 0 | -15 | -4 | 28 | -2 | -2 | -1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1103 | Bickigen - Chippis | PINT | 7 | 9 | 5 | 12 | 13 | 10 | 5 | 6 | 4 | -157 | -129 | -172 | 153 | 0 | 3 | 17 | 0 | 5 | 18 | 83 | 98 | 71 | 0 | -120 | -17 | 64 | -13 | -8 | -5 | 81 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
1104 | Niederstedem - Roost | PINT | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | -12 | 0 | -33 | 153 | 0 | 0 | 1 | 0 | 5 | 18 | 2 | 5 | 0 | 0 | -16 | -1 | -10 | -1 | -1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 49 | 73 | 22 | -15 | -7 | -27 | 32 | 36 | 29 | 195 | 341 | 90 | 18 | 0 | 0 | 0 | 0 | 0 | 2 | 538 | 549 | 522 | 0 | 96 | 9 | 38 | 7 | 5 | 3 | 81 | 4 | N/A | N/A | N/A | N/A | N/A | N/A
1106 | Bornholm Energy Island (BEI) | TOOT | 172 | 184 | 157 | 161 | 165 | 158 | 452 | 466 | 442 | -2061 | -2023 | -2119 | 153 | 0 | 45 | 229 | 0 | 5 | 18 | 7973 | 8002 | 7938 | 2000 | -1887 | -188 | -156 | -174 | -121 | -55 | 479 | 25 | N/A | N/A | N/A | N/A | N/A | N/A
1107 | EuroAfrica Interconnector | PINT | 40 | 43 | 36 | 45 | 45 | 45 | 31 | 32 | 30 | -571 | -571 | -571 | -35 | 0 | 13 | 63 | 0 | -1 | -4 | 558 | 572 | 544 | 0 | -24 | -2 | -62 | 0 | -2 | 0 | -109 | -6 | N/A | N/A | N/A | N/A | N/A | N/A
1109 | Basilicata - Campania reinforcements | PINT | 8 | 8 | 8 | 4 | 5 | 2 | 13 | 14 | 11 | -45 | -25 | -65 | -14 | 0 | 1 | 5 | 0 | 0 | -2 | 206 | 210 | 202 | 0 | -61 | -7 | -15 | -4 | -3 | -2 | -47 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1110 | Sicily - Calabria | PINT | 6 | 9 | 3 | 1 | 3 | -1 | 2 | 3 | 2 | -12 | 11 | -34 | 9 | 0 | 0 | 1 | 0 | 0 | 1 | 34 | 41 | 28 | 0 | -1 | 1 | -11 | 0 | 0 | 0 | 30 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1112 | GRITA 2 | PINT | 51 | 53 | 50 | 19 | 21 | 16 | 41 | 45 | 39 | -238 | -207 | -268 | 12 | 0 | 5 | 26 | 0 | 0 | 1 | 699 | 723 | 684 | 0 | -246 | -27 | -41 | -18 | -12 | -8 | 43 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 352 | 352 | 352 | 109 | 109 | 109 | 376 | 376 | 376 | -1397 | -1397 | -1397 | -35 | 0 | 31 | 155 | 0 | -1 | -4 | 6799 | 6799 | 6799 | 3000 | [6 empty] | -134 | -6 | N/A | N/A | N/A | N/A | N/A | N/A
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 89 | 89 | 89 | 29 | 29 | 29 | 96 | 96 | 96 | -374 | -374 | -374 | -21 | 0 | 8 | 42 | 0 | 0 | -2 | 1736 | 1736 | 1736 | 750 | [6 empty] | -67 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 75 | 75 | 75 | 23 | 23 | 23 | 75 | 75 | 75 | -289 | -289 | -289 | -22 | 0 | 6 | 32 | 0 | 0 | -2 | 1351 | 1351 | 1351 | 600 | [6 empty] | -64 | -4 | N/A | N/A | N/A | N/A | N/A | N/A
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 205 | 218 | 192 | 49 | 50 | 47 | 284 | 290 | 279 | -624 | -601 | -643 | 118 | 0 | 14 | 69 | 0 | 3 | 13 | 5146 | 5261 | 5052 | 1250 | -721 | -71 | -187 | -54 | -35 | -22 | 493 | 21 | N/A | N/A | N/A | N/A | N/A | N/A
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 205 | 218 | 192 | 49 | 50 | 47 | 284 | 290 | 279 | -624 | -601 | -643 | 130 | 0 | 14 | 69 | 0 | 3 | 14 | 5146 | 5261 | 5052 | 1250 | -721 | -71 | -187 | -54 | -35 | -22 | 516 | 23 | N/A | N/A | N/A | N/A | N/A | N/A
1124 | Offshore Wind Connection South Britanny | TOOT | 117 | 134 | 101 | 29 | 30 | 26 | 179 | 197 | 167 | -367 | -334 | -387 | 11 | 0 | 8 | 41 | 0 | 0 | 1 | 3036 | 3084 | 2993 | 750 | -434 | -44 | -93 | -34 | -22 | -13 | 52 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1125 | Offshore Wind Connection Occitanie | TOOT | 117 | 134 | 101 | 29 | 30 | 26 | 179 | 197 | 167 | -367 | -334 | -387 | -4 | 0 | 8 | 41 | 0 | 0 | 0 | 3036 | 3084 | 2993 | 750 | -434 | -44 | -93 | -34 | -22 | -13 | -29 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1126 | Offshore Wind Connection PACA | TOOT | 117 | 134 | 101 | 29 | 30 | 26 | 179 | 197 | 167 | -367 | -334 | -387 | -18 | 0 | 8 | 41 | 0 | 0 | -2 | 3036 | 3084 | 2993 | 750 | -434 | -44 | -93 | -34 | -22 | -13 | -98 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1127 | Offshore Wind Connection South Atlantic | PINT | 202 | 209 | 192 | 48 | 51 | 47 | 293 | 313 | 279 | -615 | -596 | -649 | 87 | 0 | 14 | 68 | 0 | 2 | 10 | 4967 | 5076 | 4768 | 1250 | -717 | -67 | -240 | -52 | -35 | -20 | 387 | 16 | N/A | N/A | N/A | N/A | N/A | N/A
1129 | New RES at Minho region | TOOT | 26 | 32 | 16 | 7 | 7 | 7 | 36 | 38 | 35 | -89 | -84 | -94 | 9 | 0 | 2 | 10 | 0 | 0 | 1 | 617 | 640 | 578 | 400 | -56 | -11 | 51 | -5 | -3 | -3 | 55 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1001st | Kaunertal Extension Project | PINT | 36 | 44 | 31 | 14 | 18 | 12 | 13 | 24 | 0 | -180 | -150 | -236 | -18 | 0 | 4 | 20 | 0 | 0 | -2 | 224 | 426 | 7 | 0 | -255 | -26 | -50 | -20 | -13 | -8 | -34 | -3 | N/A | N/A | N/A | N/A | N/A | N/A
1003st | Hydro pump storage in Bulgaria - Yadenitsa | PINT | 46 | 51 | 37 | 21 | 26 | 13 | 16 | 18 | 14 | -263 | -161 | -338 | -1331 | 0 | 6 | 29 | 0 | -29 | -148 | 264 | 279 | 254 | 0 | -234 | -25 | -46 | -17 | -11 | -8 | -1100 | -229 | N/A | N/A | N/A | N/A | N/A | N/A
1004st | Estonian Pumped-Hydro Energy Storage (please note the name of the Project has been changed due to location change) | PINT | 13 | 19 | 10 | 2 | 3 | 2 | 20 | 26 | 16 | -30 | -22 | -36 | -4 | 0 | 1 | 3 | N/A | 0 | N/A | 346 | 465 | 250 | 0 | -20 | 6 | -191 | 2 | -2 | 2 | -87 | -1 | N/A | N/A | N/A | N/A | N/A | N/A
1006st | HPS AMFILOCHIA | PINT | 21 | 24 | 17 | 8 | 17 | 2 | 24 | 27 | 20 | -103 | -28 | -216 | -1330 | 0 | 2 | 11 | 0 | -29 | -148 | 410 | 494 | 361 | 0 | -121 | -10 | -63 | -8 | -5 | -3 | -1098 | -229 | N/A | N/A | N/A | N/A | N/A | N/A
1012st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | TOOT | 38 | 42 | 30 | 15 | 20 | 12 | 46 | 47 | 45 | -198 | -148 | -254 | 10 | 0 | 4 | 22 | 0 | 0 | 1 | 785 | 824 | 718 | 0 | 169 | 20 | -3 | 14 | 9 | 6 | 41 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1013st | CAES Zuidwending, NL | PINT | 9 | 15 | 3 | 9 | 11 | 8 | 6 | 8 | 3 | -117 | -96 | -138 | 673 | 0 | 3 | 13 | 0 | 15 | 75 | 94 | 138 | 50 | 0 | -200 | -3 | -284 | -12 | -17 | -1 | 1976 | 117 | N/A | N/A | N/A | N/A | N/A | N/A
1025st | Silvermines Hydroelectric Power Station | PINT | 9 | 14 | 6 | 2 | 3 | 1 | 8 | 13 | 0 | -25 | -18 | -34 | 3 | 0 | 1 | 3 | 0 | 0 | 0 | 138 | 217 | 0 | 0 | -9 | 0 | -25 | 1 | -1 | 0 | 27 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1026st | Hydro pumped storage Riedl | PINT | 13 | 20 | 7 | 7 | 11 | 4 | 7 | 10 | 4 | -94 | -48 | -141 | 10 | 0 | 2 | 10 | 0 | 0 | 1 | 119 | 177 | 58 | 0 | -175 | -5 | -195 | -12 | -13 | -1 | 86 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1027st | P-PHES CUA | PINT | 26 | 31 | 16 | 7 | 14 | 1 | 27 | 28 | 23 | -93 | -15 | -173 | 18 | 0 | 2 | 10 | 0 | 0 | 2 | 447 | 502 | 408 | 0 | -128 | -13 | -30 | -9 | -6 | -4 | 33 | 3 | N/A | N/A | N/A | N/A | N/A | N/A
1035st | Ptolemaida Battery Energy Storage System | PINT | 15 | 21 | 7 | 5 | 8 | 1 | 8 | 14 | 5 | -58 | -9 | -100 | -1331 | 0 | 1 | 6 | 0 | -29 | -148 | 144 | 255 | 77 | 0 | -77 | -6 | -32 | -6 | -4 | -2 | -1103 | -228 | N/A | N/A | N/A | N/A | N/A | N/A
1037st | ELSEA - European Large Scale Energy Accumulation | PINT | 6 | 10 | 0 | -2 | -1 | -2 | 3 | 6 | 0 | 23 | 29 | 14 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 112 | 7 | 0 | -15 | 1 | -40 | 0 | -1 | 0 | -4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1038st | CAES Zuidwending Extension | PINT | 10 | 15 | 5 | 9 | 12 | 6 | 6 | 8 | 4 | -115 | -71 | -159 | 659 | 0 | 3 | 13 | 0 | 14 | 73 | 101 | 140 | 61 | 0 | -203 | -6 | -250 | -13 | -18 | -2 | 1957 | 115 | N/A | N/A | N/A | N/A | N/A | N/A
1039st | Reversible Hydraulic Power Plant Los Guajares | TOOT | 10 | 19 | 0 | 2 | 5 | -3 | 10 | 18 | 0 | -22 | 38 | -66 | -9 | 0 | 0 | 2 | 0 | 0 | -1 | 172 | 321 | 0 | 0 | -92 | -7 | -53 | -6 | -4 | -2 | -58 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1041st | Purifying – Pumped Hydroelectric Energy Storage “Velilla del Río Carrión” (P-PHES VELILLA) | PINT | 12 | 18 | 8 | 0 | 3 | -4 | 10 | 11 | 8 | -5 | 47 | -39 | 4 | 0 | 0 | 1 | 0 | 0 | 0 | 165 | 195 | 140 | 0 | -59 | -2 | -56 | -4 | -3 | -1 | 10 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1044st | Green Hydrogen Hub CAES | PINT | 15 | 25 | 6 | 10 | 14 | 5 | 8 | 14 | 2 | -125 | -67 | -182 | 2 | 0 | 3 | 14 | 0 | 0 | 0 | 145 | 254 | 35 | 0 | -303 | -8 | -367 | -19 | -19 | -2 | 3 | 0 | N/A | N/A | N/A | N/A | N/A | N/A
1046st | Online Grid Controller “PSKW-Rio” | PINT | 12 | 22 | 6 | 6 | 9 | 4 | 7 | 10 | 4 | -77 | -53 | -111 | -27 | 0 | 2 | 9 | 0 | -1 | -3 | 126 | 163 | 60 | 0 | -149 | -4 | -171 | -10 | -11 | -1 | -68 | -5 | N/A | N/A | N/A | N/A | N/A | N/A
1048st | WSK PULS (PHES) | PINT | 19 | 26 | 6 | 5 | 9 | 2 | 7 | 9 | 6 | -68 | -26 | -110 | -13 | 0 | 1 | 8 | 0 | 0 | -1 | 121 | 150 | 92 | 0 | -186 | -6 | -203 | -12 | -13 | -2 | -30 | -2 | N/A | N/A | N/A | N/A | N/A | N/A
1050st | SE Integrator | PINT | 9 | 11 | 5 | 7 | 11 | 2 | 1 | 2 | 0 | -95 | -32 | -146 | 8 | 0 | 2 | 11 | 0 | 0 | 1 | 20 | 31 | 3 | 0 | -137 | -10 | -70 | -10 | -8 | -3 | 31 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1052st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES BUSEIRO) | PINT | 17 | 24 | 12 | 4 | 7 | 2 | 12 | 13 | 11 | -48 | -19 | -86 | 11 | 0 | 1 | 5 | 0 | 0 | 1 | 203 | 225 | 164 | 0 | -78 | -8 | -25 | -5 | -4 | -2 | 25 | 2 | N/A | N/A | N/A | N/A | N/A | N/A
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 67 | 76 | 62 | 21 | 26 | 14 | 72 | 74 | 69 | -267 | -185 | -337 | 41 | 0 | 6 | 30 | 0 | 1 | 5 | 1223 | 1331 | 1054 | 0 | -258 | -29 | -34 | -20 | -13 | -9 | 98 | 7 | N/A | N/A | N/A | N/A | N/A | N/A
1055st | CAES Leer, Germany | PINT | 10 | 18 | 2 | 9 | 11 | 6 | 11 | 18 | 5 | -110 | -77 | -144 | 4 | 0 | 2 | 12 | 0 | 0 | 0 | 195 | 308 | 83 | 0 | -211 | -1 | -300 | -14 | -18 | -1 | 9 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1056st | CAES Etzel, Germany | PINT | 11 | 19 | 2 | 9 | 11 | 6 | 11 | 18 | 4 | -112 | -77 | -146 | 5 | 0 | 2 | 12 | 0 | 0 | 1 | 187 | 308 | 66 | 0 | -203 | -4 | -262 | -13 | -17 | -1 | 11 | 1 | N/A | N/A | N/A | N/A | N/A | N/A
1057st | CAES Harsefeld-Stade, Germany | PINT | 9 | 16 | 2 | 8 | 10 | 6 | 11 | 18 | 4 | -105 | -77 | -134 | 4 | 0 | 2 | 12 | 0 | 0 | 0 | 185 | 308 | 63 | 0 | -199 | -3 | -272 | -12 | -16 | -1 | 10 | 1 | N/A | N/A | N/A | N/A | N/A | N/A

## DE2040_EU
Scenario | DE2040
[16 empty] | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 75 | 82 | 64 | 11 | 14 | 7 | 67 | 77 | 60 | -93 | -59 | -116 | N/A | 3 | 14 | 35 | N/A | N/A | N/A | 1435 | 1643 | 1270 | 1154 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4 | Interconnection Portugal-Spain | TOOT | 38 | 53 | 23 | 6 | 9 | 3 | 30 | 36 | 22 | -52 | -26 | -72 | N/A | 2 | 8 | 20 | N/A | N/A | N/A | 638 | 763 | 486 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
16 | Biscay Gulf | TOOT | 311 | 335 | 282 | 61 | 69 | 52 | 206 | 214 | 199 | -495 | -426 | -558 | N/A | 16 | 72 | 186 | N/A | N/A | N/A | 4419 | 4553 | 4331 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
26 | Reschenpass Interconnector Project | TOOT | 74 | 80 | 71 | 14 | 16 | 10 | 30 | 33 | 26 | -112 | -85 | -127 | N/A | 4 | 16 | 42 | N/A | N/A | N/A | 648 | 710 | 536 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
28 | Italy-Montenegro | PINT | 35 | 39 | 30 | 13 | 20 | 8 | 28 | 48 | 13 | -122 | -88 | -165 | N/A | 3 | 15 | 40 | N/A | N/A | N/A | 527 | 819 | 293 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
29 | Italy-Tunisia | TOOT | 114 | 118 | 111 | -17 | -9 | -24 | 89 | 89 | 89 | 135 | 195 | 75 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 1928 | 1959 | 1896 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
33 | Central Northern Italy | TOOT | 30 | 44 | 12 | 9 | 11 | 3 | 21 | 24 | 17 | -77 | -45 | -93 | N/A | 2 | 10 | 26 | N/A | N/A | N/A | 424 | 510 | 290 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
35 | CZ Southwest-east corridor | PINT | 47 | 51 | 44 | 6 | 7 | 5 | 34 | 38 | 29 | -52 | -42 | -58 | N/A | 2 | 8 | 20 | N/A | N/A | N/A | 731 | 818 | 634 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 54 | 56 | 53 | 11 | 12 | 10 | 32 | 35 | 27 | -90 | -80 | -96 | N/A | 3 | 13 | 34 | N/A | N/A | N/A | 674 | 727 | 601 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 69 | 74 | 64 | 16 | 20 | 15 | 34 | 38 | 32 | -153 | -119 | -215 | N/A | 4 | 20 | 50 | N/A | N/A | N/A | 697 | 827 | 571 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 43 | 49 | 38 | -2 | 1 | -5 | 67 | 73 | 61 | 13 | 41 | -9 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 1444 | 1547 | 1294 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
85 | Integration of RES in Alentejo | TOOT | 10 | 15 | 6 | 0 | 3 | -1 | 7 | 10 | 4 | -3 | 11 | -22 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 155 | 206 | 75 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
94 | GerPol Improvements | TOOT | 220 | 220 | 219 | 81 | 84 | 78 | 102 | 105 | 99 | -662 | -637 | -686 | N/A | 22 | 97 | 248 | N/A | N/A | N/A | 2203 | 2222 | 2184 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
103 | Reinforcements Ring NL phase I | TOOT | 61 | 66 | 58 | 13 | 15 | 9 | 32 | 34 | 30 | -104 | -71 | -121 | N/A | 3 | 15 | 39 | N/A | N/A | N/A | 691 | 720 | 647 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
107 | Celtic Interconnector | TOOT | 208 | 215 | 205 | 32 | 33 | 30 | 99 | 102 | 94 | -258 | -242 | -268 | N/A | 9 | 38 | 97 | N/A | N/A | N/A | 2116 | 2179 | 2063 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 96 | 100 | 90 | 2 | 3 | 2 | 84 | 90 | 75 | -18 | -13 | -27 | N/A | 1 | 3 | 7 | N/A | N/A | N/A | 1791 | 1874 | 1640 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 506 | 547 | 470 | 53 | 72 | 32 | 551 | 562 | 537 | -435 | -258 | -587 | N/A | 14 | 63 | 163 | N/A | N/A | N/A | 11430 | 11952 | 10949 | 3500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 31 | 31 | 30 | -21 | -20 | -23 | 24 | 26 | 21 | 174 | 186 | 162 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 500 | 548 | 451 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
123 | LitPol Link Stage 2 | TOOT | 165 | 175 | 156 | 83 | 88 | 81 | 48 | 49 | 46 | -676 | -655 | -714 | N/A | 22 | 99 | 253 | N/A | N/A | N/A | 1014 | 1056 | 982 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
124 | NordBalt phase 2 | PINT | 42 | 52 | 34 | 2 | 4 | -2 | 40 | 48 | 32 | -15 | 16 | -37 | N/A | 0 | 2 | 6 | N/A | N/A | N/A | 846 | 988 | 693 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
126 | SE North-south short-term reinforcements | TOOT | 91 | 107 | 79 | 14 | 16 | 13 | 35 | 46 | 27 | -114 | -103 | -127 | N/A | 4 | 17 | 43 | N/A | N/A | N/A | 625 | 662 | 588 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
127 | Central Southern Italy | TOOT | 37 | 67 | 8 | 3 | 6 | 1 | 46 | 59 | 35 | -28 | -8 | -53 | N/A | 1 | 4 | 10 | N/A | N/A | N/A | 925 | 1064 | 771 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2107.3658 | 2107.3658 | 2107.3658 | 27.4939 | 27.4939 | 27.4939 | 402.6229 | 402.6229 | 402.6229 | -981 | -981 | -981 | N/A | 102.7864 | 454.7521 | 1168.0277 | N/A | N/A | N/A | 4027 | 4027 | 4027 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
132 | HVDC Line A-North | TOOT | 6299.6019 | 6299.6019 | 6299.6019 | 82.1874 | 82.1874 | 82.1874 | 1145.8795 | 1145.8795 | 1145.8795 | -2935 | -2935 | -2935 | N/A | 96.8637 | 428.5484 | 1100.7237 | N/A | N/A | N/A | 11459.6 | 11459.6 | 11459.6 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
138 | Black Sea Corridor | TOOT | 66 | 72 | 58 | 9 | 13 | 4 | 37 | 41 | 33 | -73 | -35 | -105 | N/A | 2 | 11 | 27 | N/A | N/A | N/A | 777 | 845 | 705 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
142 | CSE4 | TOOT | 48 | 50 | 47 | 8 | 11 | 6 | 24 | 26 | 22 | -62 | -45 | -90 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 508 | 580 | 472 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
144 | Mid Continental East corridor | TOOT | 75 | 76 | 74 | 16 | 21 | 14 | 77 | 86 | 71 | -134 | -111 | -169 | N/A | 4 | 20 | 50 | N/A | N/A | N/A | 1657 | 1830 | 1552 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
150 | Italy-Slovenia | light PINT | 168 | 183 | 151 | 41 | 43 | 37 | 58 | 63 | 54 | -334 | -301 | -350 | N/A | 11 | 49 | 125 | N/A | N/A | N/A | 1244 | 1380 | 1146 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
153 | France-Alderney-Britain | PINT | 87 | 97 | 75 | 7 | 7 | 6 | 72 | 74 | 70 | -53 | -50 | -58 | N/A | 2 | 8 | 20 | N/A | N/A | N/A | 1533 | 1567 | 1500 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
170 | Baltic States Synchronization with Continental Europe | TOOT | 220 | 220 | 220 | 114 | 120 | 110 | 67 | 74 | 59 | -931 | -892 | -973 | N/A | 31 | 136 | 349 | N/A | N/A | N/A | 1438 | 1590 | 1243 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
174 | Greenconnector | PINT | 102 | 111 | 93 | 34 | 37 | 29 | 47 | 48 | 44 | -278 | -238 | -299 | N/A | 9 | 41 | 104 | N/A | N/A | N/A | 1009 | 1063 | 935 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
176 | Hansa PowerBridge I | TOOT | 143 | 155 | 129 | 33 | 36 | 31 | 80 | 92 | 66 | -265 | -251 | -291 | N/A | 9 | 39 | 99 | N/A | N/A | N/A | 1708 | 1967 | 1446 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
183 | DKW-DE, Westcoast | TOOT | 94 | 95 | 92 | 26 | 28 | 24 | 61 | 68 | 56 | -211 | -194 | -227 | N/A | 7 | 31 | 79 | N/A | N/A | N/A | 1296 | 1448 | 1163 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
186 | East of Austria | TOOT | 129 | 135 | 123 | 16 | 20 | 12 | 139 | 146 | 130 | -133 | -102 | -166 | N/A | 4 | 19 | 50 | N/A | N/A | N/A | 2975 | 3085 | 2853 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
187 | St. Peter (AT) - Pleinting (DE) | PINT | 185 | 194 | 175 | 41 | 47 | 34 | 90 | 93 | 85 | -333 | -275 | -380 | N/A | 11 | 49 | 125 | N/A | N/A | N/A | 1903 | 2009 | 1797 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
190 | NorthConnect | TOOT | 0 | 0 | 0 | 28 | 35 | 21 | 77 | 120 | 30 | -226 | -171 | -285 | N/A | 7 | 33 | 85 | N/A | N/A | N/A | 1632 | 2485 | 634 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 45 | 47 | 44 | 7 | 7 | 7 | 33 | 36 | 29 | -57 | -55 | -58 | N/A | 2 | 8 | 21 | N/A | N/A | N/A | 704 | 747 | 634 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 35 | 39 | 32 | 8 | 13 | 2 | 15 | 17 | 11 | -68 | -25 | -107 | N/A | 2 | 10 | 25 | N/A | N/A | N/A | 306 | 370 | 236 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
219 | EuroAsia Interconnector | TOOT | 595 | 630 | 560 | 51 | 51 | 51 | 290 | 291 | 288 | -308 | -200 | -415 | N/A | 14 | 61 | 155 | N/A | N/A | N/A | 6264 | 6395 | 6134 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
225 | 2nd interconnector Belgium - Germany | light PINT | 112 | 118 | 108 | 22 | 23 | 21 | 70 | 73 | 67 | -177 | -170 | -189 | N/A | 6 | 26 | 66 | N/A | N/A | N/A | 1471 | 1502 | 1429 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
227 | Transbalkan Corridor | TOOT | 11 | 18 | 4 | 3 | 6 | 1 | 0 | 2 | 0 | -21 | -11 | -48 | N/A | 1 | 3 | 8 | N/A | N/A | N/A | -22 | 34 | -99 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
228 | Muhlbach - Eichstetten | TOOT | 46 | 52 | 40 | 9 | 10 | 7 | 26 | 28 | 25 | -70 | -58 | -78 | N/A | 2 | 10 | 26 | N/A | N/A | N/A | 556 | 576 | 548 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
230 | GerPol Power Bridge I | TOOT | 449 | 455 | 443 | 227 | 230 | 223 | 105 | 109 | 101 | -1844 | -1809 | -1873 | N/A | 61 | 269 | 691 | N/A | N/A | N/A | 2244 | 2313 | 2206 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
231 | Beznau - Tiengen | PINT | 7 | 15 | 0 | 10 | 17 | 7 | 46 | 51 | 38 | -85 | -56 | -140 | N/A | 3 | 12 | 32 | N/A | N/A | N/A | 982 | 1062 | 830 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 7722.5714 | 7722.5714 | 7722.5714 | 104.6552 | 104.6552 | 104.6552 | 1407.4598 | 1407.4598 | 1407.4598 | -3738 | -3738 | -3739 | N/A | 32.6665 | 144.5245 | 371.2101 | N/A | N/A | N/A | 14074.7 | 14074.7 | 14074.7 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
239 | Fenno-Skan 1 renewal | light PINT | 45 | 51 | 41 | -1 | 1 | -5 | 43 | 50 | 39 | 7 | 39 | -9 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 918 | 1042 | 857 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 11 | 14 | 8 | 1 | 2 | 0 | 10 | 13 | 7 | -6 | 1 | -15 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 217 | 264 | 146 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
244 | Vigy - Uchtelfangen area | PINT | 241 | 248 | 232 | 46 | 50 | 40 | 137 | 142 | 134 | -374 | -328 | -405 | N/A | 12 | 55 | 140 | N/A | N/A | N/A | 2848 | 2931 | 2718 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
245 | Upgrade Meeden - Diele | TOOT | 32 | 33 | 30 | 8 | 9 | 8 | 16 | 17 | 15 | -67 | -65 | -70 | N/A | 2 | 10 | 25 | N/A | N/A | N/A | 351 | 367 | 334 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
247 | AQUIND Interconnector | PINT | 127 | 137 | 110 | 10 | 12 | 8 | 93 | 109 | 78 | -83 | -64 | -98 | N/A | 3 | 12 | 31 | N/A | N/A | N/A | 1991 | 2300 | 1712 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 16 | 25 | 8 | 5 | 11 | 0 | 9 | 14 | 6 | -37 | 0 | -93 | N/A | 1 | 5 | 14 | N/A | N/A | N/A | 179 | 239 | 136 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 11 | 17 | 4 | 14 | 16 | 12 | 22 | 29 | 16 | -113 | -98 | -129 | N/A | 4 | 16 | 42 | N/A | N/A | N/A | 455 | 640 | 329 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 783.4376 | 783.4376 | 783.4376 | 5.6024 | 5.6024 | 5.6024 | 221.0578 | 221.0578 | 221.0578 | -200 | -200 | -200 | N/A | 97.452 | 431.1515 | 1107.4096 | N/A | N/A | N/A | 2211.1 | 2211.1 | 2211.1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
259 | HU-RO | PINT | 82 | 85 | 79 | 10 | 12 | 8 | 49 | 53 | 43 | -78 | -65 | -94 | N/A | 3 | 11 | 29 | N/A | N/A | N/A | 1036 | 1100 | 919 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 44 | 58 | 29 | -21 | -12 | -27 | 28 | 35 | 18 | 168 | 216 | 99 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 715 | 737 | 693 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 37 | 37 | 37 | 3 | 5 | 1 | 24 | 25 | 22 | -25 | -9 | -42 | N/A | 1 | 4 | 10 | N/A | N/A | N/A | 515 | 538 | 493 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
263 | Lake Constance East | light PINT | 108 | 120 | 90 | 38 | 43 | 33 | 70 | 75 | 66 | -309 | -266 | -353 | N/A | 10 | 45 | 116 | N/A | N/A | N/A | 1499 | 1655 | 1401 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
267 | Hansa PowerBridge II | light PINT | 104 | 105 | 104 | 29 | 30 | 27 | 66 | 74 | 56 | -237 | -221 | -248 | N/A | 8 | 35 | 89 | N/A | N/A | N/A | 1395 | 1535 | 1233 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 189 | 193 | 186 | 37 | 40 | 34 | 137 | 142 | 134 | -301 | -275 | -329 | N/A | 10 | 44 | 113 | N/A | N/A | N/A | 2944 | 3011 | 2862 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
276 | FR-ES project -Navarra-Landes | PINT | 189 | 193 | 186 | 37 | 40 | 34 | 137 | 142 | 134 | -301 | -275 | -329 | N/A | 10 | 44 | 113 | N/A | N/A | N/A | 2944 | 3011 | 2862 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 137 | 148 | 129 | 31 | 35 | 28 | 55 | 60 | 51 | -256 | -226 | -283 | N/A | 8 | 37 | 96 | N/A | N/A | N/A | 1180 | 1279 | 1122 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
283 | TuNur Italy | PINT | 36 | 70 | 0 | 39 | 80 | -1 | 0 | 0 | 0 | -311 | 19 | -652 | N/A | 10 | 46 | 118 | N/A | N/A | N/A | -1360 | 0 | -4081 | 4900 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
285 | GridLink | PINT | 87 | 97 | 75 | 7 | 7 | 6 | 72 | 74 | 70 | -53 | -50 | -58 | N/A | 2 | 8 | 20 | N/A | N/A | N/A | 1533 | 1567 | 1500 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
286 | Greenlink | PINT | 25 | 26 | 23 | 14 | 15 | 14 | 39 | 46 | 35 | -118 | -115 | -119 | N/A | 4 | 17 | 44 | N/A | N/A | N/A | 822 | 1014 | 732 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
293 | Southern Aegean Interconnector | PINT | 23 | 27 | 17 | 4 | 7 | 1 | 27 | 32 | 22 | -34 | -8 | -60 | N/A | 1 | 5 | 13 | N/A | N/A | N/A | 581 | 680 | 487 | 582 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
297 | BRABO II + III | TOOT | 37 | 37 | 37 | 5 | 8 | 1 | 23 | 25 | 21 | -38 | -9 | -62 | N/A | 1 | 5 | 14 | N/A | N/A | N/A | 490 | 538 | 440 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
299 | SACOI3 | TOOT | 93 | 104 | 81 | 27 | 30 | 22 | 43 | 48 | 41 | -223 | -181 | -247 | N/A | 7 | 33 | 84 | N/A | N/A | N/A | 930 | 1027 | 871 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
309 | NeuConnect | TOOT | 71 | 76 | 63 | 10 | 15 | 4 | 80 | 112 | 51 | -106 | -31 | -203 | N/A | 3 | 12 | 31 | N/A | N/A | N/A | 1740 | 1907 | 1565 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
312 | St. Peter (AT) - Tauern (AT) | TOOT | 252 | 262 | 236 | 53 | 59 | 49 | 124 | 127 | 122 | -432 | -396 | -480 | N/A | 14 | 63 | 162 | N/A | N/A | N/A | 2646 | 2778 | 2548 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 251 | 262 | 236 | 55 | 62 | 49 | 124 | 127 | 122 | -446 | -396 | -502 | N/A | 15 | 65 | 167 | N/A | N/A | N/A | 2631 | 2778 | 2548 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 8 | 12 | 0 | 2 | 4 | 0 | 4 | 9 | 1 | -18 | -3 | -30 | N/A | 1 | 3 | 7 | N/A | N/A | N/A | 83 | 190 | 21 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 6 | 12 | 0 | 0 | 2 | -3 | 5 | 15 | 0 | 0 | 22 | -13 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 46 | 95 | 6 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
325 | Obersielach (AT) - Podlog (SI) | PINT | 31 | 40 | 22 | 3 | 5 | -1 | 23 | 30 | 19 | -24 | 10 | -45 | N/A | 1 | 4 | 9 | N/A | N/A | N/A | 473 | 628 | 327 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
328 | Interconnector DE-LUX | TOOT | 7 | 15 | 0 | 1 | 1 | 0 | 3 | 8 | 0 | -7 | -3 | -12 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 62 | 183 | -106 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
330 | 4th 400kV CZ-SK interconnector | light PINT | 28 | 31 | 25 | 6 | 7 | 5 | 18 | 24 | 12 | -48 | -42 | -54 | N/A | 2 | 7 | 18 | N/A | N/A | N/A | 376 | 506 | 257 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
333 | PST Foretaille | PINT | 22 | 30 | 14 | 27 | 29 | 25 | 51 | 56 | 46 | -220 | -199 | -237 | N/A | 7 | 32 | 83 | N/A | N/A | N/A | 1095 | 1190 | 1023 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
335 | Project 335 - North Sea Wind Power Hub | light PINT | 245 | 266 | 229 | 278 | 286 | 266 | 1668 | 1697 | 1640 | -2260 | -2160 | -2327 | N/A | 75 | 330 | 848 | N/A | N/A | N/A | 34998 | 35147 | 34771 | 12000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
338 | Adriatic HVDC link | PINT | 156 | 203 | 124 | 38 | 40 | 35 | 69 | 77 | 65 | -274 | -210 | -327 | N/A | 10 | 45 | 115 | N/A | N/A | N/A | 1395 | 1701 | 1104 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
339 | Italian HVDC tri-terminal link | PINT | 95 | 95 | 95 | 12 | 17 | 9 | 122 | 159 | 95 | -118 | -94 | -135 | N/A | 3 | 15 | 38 | N/A | N/A | N/A | 2381 | 2690 | 2090 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
341 | North CSE Corridor | PINT | 24 | 30 | 19 | 5 | 10 | 0 | 39 | 46 | 33 | -44 | -2 | -81 | N/A | 1 | 6 | 17 | N/A | N/A | N/A | 920 | 1202 | 734 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
342 | Central Balkan Corridor | PINT | 29 | 32 | 24 | 5 | 6 | 4 | 14 | 21 | 5 | -43 | -31 | -52 | N/A | 1 | 6 | 16 | N/A | N/A | N/A | 297 | 452 | 114 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
343 | CSE1 New | PINT | 7 | 12 | 2 | 0 | 2 | -2 | 3 | 5 | 2 | -2 | 20 | -17 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 66 | 95 | 38 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
344 | Reinforcements Ring NL phase II | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
345 | 3rd circuit Diemen-Lelystad-Ens | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
346 | ZuidWest380 NL Oost | PINT | 37 | 37 | 37 | 5 | 8 | 1 | 23 | 25 | 21 | -38 | -9 | -62 | N/A | 1 | 5 | 14 | N/A | N/A | N/A | 490 | 538 | 440 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
347 | 3rd circuit Krimpen a/d IJssel - Geertruidenberg | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
348 | NoordWest380 NL | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
349 | MaresConnect | PINT | 44 | 55 | 33 | 19 | 21 | 18 | 55 | 60 | 51 | -158 | -148 | -169 | N/A | 5 | 23 | 59 | N/A | N/A | N/A | 1187 | 1328 | 1077 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
350 | South Balkan Corridor | TOOT | 7 | 15 | 0 | 5 | 11 | 1 | 5 | 10 | 2 | -42 | -11 | -91 | N/A | 1 | 6 | 16 | N/A | N/A | N/A | 117 | 221 | 32 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 121 | 129 | 115 | 26 | 28 | 22 | 53 | 55 | 51 | -211 | -183 | -228 | N/A | 7 | 31 | 79 | N/A | N/A | N/A | 1013 | 1209 | 747 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 0 | 0 | 0 | 0 | 1 | -1 | 3 | 4 | 2 | -2 | 8 | -7 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 70 | 82 | 48 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 36 | 37 | 32 | 6 | 8 | 5 | 21 | 22 | 19 | -48 | -41 | -62 | N/A | 2 | 7 | 18 | N/A | N/A | N/A | 449 | 493 | 416 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7513.2791 | 7513.2791 | 7513.2791 | 104.9593 | 104.9593 | 104.9593 | 1422.255 | 1422.255 | 1422.255 | -3749 | -3749 | -3749 | N/A | 53.147 | 235.1354 | 603.9436 | N/A | N/A | N/A | 14223.5 | 14223.5 | 14223.5 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1039 | SE North-south long-term reinforcements | light PINT | 21 | 22 | 20 | 5 | 8 | 3 | 11 | 17 | 8 | -40 | -24 | -65 | N/A | 1 | 6 | 15 | N/A | N/A | N/A | 238 | 366 | 165 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1040 | LirIC | PINT | 40 | 49 | 33 | 15 | 16 | 13 | 21 | 23 | 18 | -119 | -104 | -131 | N/A | 4 | 17 | 45 | N/A | N/A | N/A | 448 | 497 | 371 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1041 | GREGY Green Energy Interconnector | PINT | 644 | 649 | 638 | -47 | -9 | -113 | 403 | 420 | 390 | 379 | 921 | 73 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 8670 | 9257 | 8258 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1042 | Offshore Wind LT 1 | PINT | 27 | 33 | 20 | 1 | 2 | 0 | 37 | 46 | 32 | -11 | 1 | -17 | N/A | 0 | 1 | 4 | N/A | N/A | N/A | 813 | 979 | 670 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 92 | 109 | 80 | 16 | 18 | 13 | 52 | 55 | 48 | -128 | -103 | -144 | N/A | 4 | 19 | 48 | N/A | N/A | N/A | 1118 | 1170 | 1062 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 593 | 608 | 580 | -10 | -2 | -19 | 472 | 485 | 461 | 82 | 154 | 13 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 10089 | 10232 | 9908 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 32 | 32 | 32 | -13 | -5 | -17 | 4 | 10 | 1 | 102 | 135 | 44 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 92 | 208 | 18 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1050 | Tarchon Energy Ltd | PINT | 63 | 77 | 52 | 9 | 10 | 7 | 68 | 69 | 67 | -70 | -57 | -80 | N/A | 2 | 10 | 26 | N/A | N/A | N/A | 1436 | 1455 | 1416 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1051 | Aminth Energy Ltd | PINT | 80 | 82 | 78 | 12 | 13 | 12 | 95 | 99 | 92 | -100 | -95 | -107 | N/A | 3 | 15 | 38 | N/A | N/A | N/A | 2047 | 2113 | 2013 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1052 | Lienz (AT) - Obersielach (AT) | PINT | 44 | 49 | 39 | 6 | 9 | 5 | 36 | 45 | 31 | -52 | -39 | -70 | N/A | 2 | 8 | 19 | N/A | N/A | N/A | 780 | 940 | 680 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 70 | 74 | 64 | 16 | 18 | 15 | 34 | 38 | 31 | -134 | -119 | -148 | N/A | 4 | 20 | 50 | N/A | N/A | N/A | 724 | 827 | 660 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 178 | 182 | 172 | 12 | 14 | 10 | 136 | 137 | 136 | -95 | -84 | -114 | N/A | 3 | 14 | 36 | N/A | N/A | N/A | 2810 | 2905 | 2655 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1058 | HVDC Interconnector DE-CH | light PINT | 27 | 31 | 20 | 28 | 31 | 23 | 74 | 77 | 69 | -230 | -187 | -254 | N/A | 8 | 34 | 86 | N/A | N/A | N/A | 1584 | 1653 | 1519 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1059 | Southern Italy | PINT | 5 | 9 | 1 | 0 | 1 | -2 | 8 | 12 | 1 | 4 | 18 | -8 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 157 | 234 | 12 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1063 | ZuidWest380 West | PINT | 34 | 37 | 30 | 4 | 5 | 3 | 23 | 24 | 22 | -32 | -22 | -42 | N/A | 1 | 5 | 12 | N/A | N/A | N/A | 504 | 516 | 493 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1066 | Bulgaria - Turkey | light PINT | 234 | 234 | 233 | -19 | -17 | -22 | 116 | 116 | 116 | 157 | 176 | 138 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 2464 | 2466 | 2461 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 142 | 150 | 130 | -12 | -7 | -15 | 88 | 93 | 83 | 95 | 123 | 56 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 1887 | 2044 | 1771 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1068 | LaSGo Link | light PINT | 34 | 45 | 22 | 3 | 9 | 0 | 31 | 36 | 27 | -28 | 2 | -75 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 670 | 778 | 596 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1074 | Pannonian Corridor | PINT | 11 | 16 | 8 | 5 | 6 | 4 | 13 | 14 | 11 | -41 | -35 | -52 | N/A | 1 | 6 | 15 | N/A | N/A | N/A | 275 | 315 | 228 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1082 | Sea-Socket | light PINT | 61 | 70 | 56 | 8 | 9 | 7 | 73 | 76 | 72 | -63 | -59 | -69 | N/A | 2 | 9 | 24 | N/A | N/A | N/A | 1574 | 1600 | 1527 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1085 | Malta-Italy Cable Link No.2 | PINT | 21 | 27 | 12 | 12 | 13 | 9 | 6 | 7 | 5 | -95 | -73 | -107 | N/A | 3 | 14 | 36 | N/A | N/A | N/A | 133 | 144 | 115 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 36 | 39 | 34 | 1 | 1 | 1 | 36 | 39 | 33 | -9 | -9 | -9 | N/A | 0 | 1 | 3 | N/A | N/A | N/A | 774 | 816 | 709 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1088 | Off-shore Wind Park in Latvia and Estonia - ELWIND | PINT | 0 | 0 | 0 | 2 | 2 | 1 | 63 | 65 | 61 | -13 | -10 | -14 | N/A | 0 | 2 | 5 | N/A | N/A | N/A | 1330 | 1367 | 1287 | 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1092 | Offshore Hybrid HVDC Interconnector BEDK | PINT | 339 | 341 | 336 | 84 | 86 | 81 | 441 | 455 | 434 | -681 | -661 | -701 | N/A | 22 | 99 | 255 | N/A | N/A | N/A | 9269 | 9409 | 9168 | 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1094 | Estlink 3 | light PINT | 39 | 42 | 34 | 4 | 5 | 3 | 33 | 35 | 29 | -33 | -26 | -41 | N/A | 1 | 5 | 12 | N/A | N/A | N/A | 702 | 731 | 646 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 62 | 78 | 46 | -2 | 1 | -5 | 64 | 78 | 54 | 15 | 39 | -12 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 1361 | 1617 | 1184 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1096 | Beznau - Mettlen | PINT | 12 | 13 | 11 | 15 | 22 | 10 | 54 | 59 | 48 | -124 | -80 | -182 | N/A | 4 | 18 | 47 | N/A | N/A | N/A | 1155 | 1252 | 1062 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1097 | Upgrade to Konti-Skan | PINT | 75 | 93 | 57 | 12 | 16 | 9 | 50 | 60 | 44 | -97 | -75 | -131 | N/A | 3 | 14 | 36 | N/A | N/A | N/A | 1075 | 1274 | 933 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1098 | Offshore Wind LT 2 | PINT | 29 | 33 | 22 | 1 | 2 | 0 | 36 | 46 | 32 | -10 | 1 | -17 | N/A | 0 | 2 | 4 | N/A | N/A | N/A | 697 | 719 | 670 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 26 | 29 | 21 | 2 | 3 | 0 | 27 | 35 | 17 | -14 | 4 | -25 | N/A | 0 | 2 | 5 | N/A | N/A | N/A | 589 | 760 | 380 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1102 | Mettlen - Ulrichen | light PINT | 5 | 7 | 4 | 3 | 6 | 1 | 15 | 16 | 12 | -27 | -6 | -49 | N/A | 1 | 4 | 10 | N/A | N/A | N/A | 317 | 340 | 273 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1103 | Bickigen - Chippis | PINT | 11 | 16 | 8 | 11 | 16 | 8 | 37 | 39 | 34 | -90 | -67 | -128 | N/A | 3 | 13 | 34 | N/A | N/A | N/A | 783 | 805 | 747 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1104 | Niederstedem - Roost | PINT | 2 | 5 | 0 | 1 | 3 | 0 | 1 | 2 | 0 | -7 | 0 | -21 | N/A | 0 | 1 | 3 | N/A | N/A | N/A | 18 | 47 | 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 114 | 127 | 101 | 15 | 18 | 13 | 14 | 25 | 4 | -166 | -105 | -227 | N/A | 4 | 18 | 47 | N/A | N/A | N/A | 392 | 700 | 85 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1106 | Bornholm Energy Island (BEI) | TOOT | 76 | 77 | 75 | 37 | 41 | 29 | 248 | 285 | 226 | -298 | -238 | -335 | N/A | 10 | 43 | 112 | N/A | N/A | N/A | 5227 | 6069 | 4780 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1107 | EuroAfrica Interconnector | PINT | 108 | 109 | 108 | 4 | 9 | -3 | 30 | 37 | 22 | -30 | 28 | -73 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 656 | 794 | 470 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1109 | Basilicata - Campania reinforcements | PINT | 12 | 13 | 11 | -1 | 0 | -2 | 19 | 26 | 13 | 6 | 14 | 1 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 371 | 434 | 282 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1110 | Sicily - Calabria | PINT | 5 | 6 | 3 | 0 | 1 | -3 | 5 | 6 | 5 | 3 | 23 | -9 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 111 | 128 | 81 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1112 | GRITA 2 | PINT | 73 | 98 | 46 | 9 | 14 | 1 | 39 | 48 | 32 | -74 | -9 | -114 | N/A | 2 | 11 | 27 | N/A | N/A | N/A | 790 | 873 | 706 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 127 | 127 | 127 | 25 | 25 | 25 | 157 | 157 | 157 | -203 | -203 | -203 | N/A | 7 | 30 | 76 | N/A | N/A | N/A | 3311 | 3311 | 3311 | 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 27 | 27 | 27 | 8 | 8 | 8 | 34 | 34 | 34 | -61 | -61 | -61 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 725 | 725 | 725 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 16 | 16 | 16 | 3 | 3 | 3 | 30 | 30 | 30 | -27 | -27 | -27 | N/A | 1 | 4 | 10 | N/A | N/A | N/A | 619 | 619 | 619 | 600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 132 | 135 | 130 | 13 | 16 | 11 | 165 | 170 | 157 | -107 | -92 | -129 | N/A | 4 | 16 | 40 | N/A | N/A | N/A | 3535 | 3600 | 3456 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 132 | 135 | 130 | 13 | 16 | 11 | 165 | 170 | 157 | -107 | -92 | -129 | N/A | 4 | 16 | 40 | N/A | N/A | N/A | 3535 | 3600 | 3456 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1124 | Offshore Wind Connection South Britanny | TOOT | 81 | 83 | 80 | 8 | 9 | 7 | 100 | 102 | 95 | -63 | -56 | -70 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 2144 | 2180 | 2099 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1125 | Offshore Wind Connection Occitanie | TOOT | 81 | 83 | 80 | 8 | 9 | 7 | 100 | 102 | 95 | -63 | -56 | -70 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 2144 | 2180 | 2099 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1126 | Offshore Wind Connection PACA | TOOT | 81 | 83 | 80 | 8 | 9 | 7 | 100 | 102 | 95 | -63 | -56 | -70 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 2144 | 2180 | 2099 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1127 | Offshore Wind Connection South Atlantic | PINT | 134 | 135 | 132 | 13 | 16 | 11 | 165 | 170 | 157 | -107 | -92 | -129 | N/A | 4 | 16 | 40 | N/A | N/A | N/A | 3533 | 3596 | 3456 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1129 | New RES at Minho region | TOOT | 22 | 27 | 18 | 1 | 3 | -2 | 24 | 30 | 20 | -5 | 17 | -21 | N/A | 0 | 1 | 2 | N/A | N/A | N/A | 506 | 642 | 433 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1001st | Kaunertal Extension Project | PINT | 60 | 61 | 60 | 8 | 12 | 3 | 45 | 66 | 19 | -63 | -24 | -96 | N/A | 2 | 9 | 24 | N/A | N/A | N/A | 970 | 1409 | 415 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1003st | Hydro pump storage in Bulgaria - Yadenitsa | PINT | 84 | 95 | 77 | 13 | 19 | 8 | 68 | 82 | 57 | -105 | -67 | -158 | N/A | 3 | 15 | 39 | N/A | N/A | N/A | 1464 | 1719 | 1257 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1004st | Estonian Pumped-Hydro Energy Storage (please note the name of the Project has been changed due to location change) | PINT | 16 | 20 | 9 | 4 | 9 | 0 | 18 | 22 | 15 | -29 | 2 | -71 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 398 | 483 | 321 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1006st | HPS AMFILOCHIA | PINT | 57 | 62 | 54 | 8 | 11 | 5 | 59 | 65 | 55 | -63 | -43 | -87 | N/A | 2 | 9 | 24 | N/A | N/A | N/A | 1278 | 1376 | 1170 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1012st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | TOOT | 55 | 57 | 51 | 8 | 9 | 6 | 56 | 62 | 53 | -61 | -51 | -75 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 1208 | 1320 | 1117 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1013st | CAES Zuidwending, NL | PINT | 9 | 16 | 2 | 8 | 13 | 2 | 9 | 11 | 8 | -61 | -16 | -106 | N/A | 2 | 9 | 23 | N/A | N/A | N/A | 198 | 226 | 170 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1025st | Silvermines Hydroelectric Power Station | PINT | 15 | 19 | 10 | 4 | 10 | 0 | 10 | 14 | 7 | -29 | -1 | -79 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 218 | 301 | 156 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1026st | Hydro pumped storage Riedl | PINT | 23 | 31 | 17 | 3 | 5 | 0 | 16 | 28 | 6 | -22 | -3 | -37 | N/A | 1 | 3 | 8 | N/A | N/A | N/A | 345 | 579 | 120 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1027st | P-PHES CUA | PINT | 25 | 40 | 10 | 3 | 4 | 2 | 34 | 43 | 19 | -21 | -14 | -30 | N/A | 1 | 3 | 8 | N/A | N/A | N/A | 877 | 914 | 841 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1035st | Ptolemaida Battery Energy Storage System | PINT | 14 | 16 | 12 | 4 | 7 | 1 | 18 | 26 | 12 | -31 | -12 | -58 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 381 | 552 | 264 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1036st | SR Mar de Aragon | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1037st | ELSEA - European Large Scale Energy Accumulation | PINT | 6 | 9 | 2 | 2 | 5 | -1 | 5 | 10 | 1 | -16 | 12 | -41 | N/A | 1 | 2 | 6 | N/A | N/A | N/A | 116 | 211 | 22 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1038st | CAES Zuidwending Extension | PINT | 8 | 15 | 2 | 7 | 12 | 2 | 8 | 9 | 8 | -57 | -20 | -95 | N/A | 2 | 8 | 21 | N/A | N/A | N/A | 177 | 183 | 171 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1039st | Reversible Hydraulic Power Plant Los Guajares | TOOT | 19 | 19 | 19 | 0 | 3 | -4 | 21 | 22 | 20 | 3 | 31 | -21 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 439 | 480 | 417 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1041st | Purifying – Pumped Hydroelectric Energy Storage “Velilla del Río Carrión” (P-PHES VELILLA) | PINT | 1 | 1 | 0 | -1 | 2 | -4 | 11 | 14 | 6 | 12 | 36 | -20 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 238 | 293 | 130 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1044st | Green Hydrogen Hub CAES | PINT | 7 | 12 | 2 | 4 | 8 | 0 | 7 | 8 | 6 | -32 | 1 | -65 | N/A | 1 | 5 | 12 | N/A | N/A | N/A | 144 | 158 | 131 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1046st | Online Grid Controller “PSKW-Rio” | Light PINT | 17 | 19 | 14 | 2 | 4 | 0 | 18 | 28 | 10 | -20 | -2 | -34 | N/A | 1 | 3 | 8 | N/A | N/A | N/A | 370 | 576 | 201 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048st | WSK PULS (PHES) | PINT | 19 | 25 | 14 | 4 | 10 | 0 | 22 | 28 | 13 | -30 | 3 | -78 | N/A | 1 | 4 | 11 | N/A | N/A | N/A | 470 | 576 | 293 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1050st | SE Integrator | PINT | 16 | 25 | 11 | 5 | 9 | 3 | 9 | 15 | 5 | -43 | -25 | -72 | N/A | 1 | 6 | 16 | N/A | N/A | N/A | 194 | 337 | 103 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1052st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES BUSEIRO) | PINT | 10 | 15 | 1 | 0 | 1 | -1 | 13 | 17 | 7 | 1 | 10 | -10 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 275 | 378 | 157 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 72 | 78 | 63 | 6 | 10 | 4 | 91 | 99 | 87 | -52 | -30 | -79 | N/A | 2 | 8 | 19 | N/A | N/A | N/A | 1959 | 2112 | 1852 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1055st | CAES Leer, Germany | PINT | 22 | 29 | 14 | 10 | 11 | 8 | 15 | 24 | 7 | -79 | -68 | -91 | N/A | 3 | 12 | 30 | N/A | N/A | N/A | 320 | 493 | 147 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1056st | CAES Etzel, Germany | PINT | 23 | 29 | 18 | 11 | 13 | 8 | 15 | 24 | 7 | -87 | -68 | -107 | N/A | 3 | 13 | 33 | N/A | N/A | N/A | 314 | 493 | 135 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057st | CAES Harsefeld-Stade, Germany | PINT | 23 | 29 | 17 | 10 | 13 | 8 | 15 | 24 | 7 | -85 | -68 | -102 | N/A | 3 | 12 | 32 | N/A | N/A | N/A | 317 | 493 | 140 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A

## DE2030GS_EU
Scenario | DE2030GS
[16 empty] | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg
Project ID | Project name | Chosen Approach | ΔSEW |  |  | ΔSEW_CO2 |  |  | ΔSEW_RES |  |  | ΔCO2_market |  |  | ΔCO2_network | ΔCO2_market_SEW |  |  | ΔCO2_network_SEW |  |  | ΔRES |  |  | ΔRES_MW | ΔNOx | ΔNH3 | ΔSO2 | ΔPM5 | ΔPM10 | ΔNMVOC | Δlosses | Δlosses_monetized | ΔSoS |  |  | ΔSoS_monetized
|  |  | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | max | min | weighted avg | low | mid | high | low | mid | high | weighted avg | max | min | Explicit | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | weighted avg | max | min | weighted avg | max | min
|  |  | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | ktonnes / year | ktonnes / year | ktonnes / year | ktonnes / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | M€ / year | GWh/ year | GWh/ year | GWh/ year | MW | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | tonnes / year | GWh / year | M€ / year | MWh / year | MWh / year | MWh / year | M€ / year | M€ / year | M€ / year
1 | RES in north of Portugal | TOOT | 95 | 99 | 89 | 23 | 27 | 17 | 73 | 75 | 71 | -297 | -214 | -347 | N/A | 0 | 7 | 33 | N/A | N/A | N/A | 936 | 978 | 894 | 1154 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4 | Interconnection Portugal-Spain | TOOT | 35 | 46 | 25 | 10 | 14 | 4 | 22 | 39 | 8 | -128 | -56 | -181 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 280 | 487 | 108 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
16 | Biscay Gulf | TOOT | 505 | 545 | 474 | 97 | 117 | 70 | 412 | 425 | 400 | -1248 | -896 | -1498 | N/A | 0 | 27 | 139 | N/A | N/A | N/A | 5308 | 5373 | 5211 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
26 | Reschenpass Interconnector Project | TOOT | 46 | 63 | 34 | 12 | 16 | 11 | 6 | 7 | 4 | -160 | -137 | -203 | N/A | 0 | 3 | 17 | N/A | N/A | N/A | 71 | 92 | 53 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
28 | Italy-Montenegro | PINT | 25 | 25 | 25 | 10 | 11 | 9 | 31 | 35 | 27 | -136 | -115 | -157 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 395 | 445 | 344 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
29 | Italy-Tunisia | TOOT | 84 | 108 | 59 | -71 | -60 | -85 | 67 | 74 | 57 | 812 | 854 | 770 | N/A | 16 | 0 | 0 | N/A | N/A | N/A | 862 | 943 | 727 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
33 | Central Northern Italy | TOOT | 42 | 43 | 41 | 15 | 18 | 14 | 21 | 23 | 16 | -200 | -175 | -228 | N/A | 0 | 4 | 21 | N/A | N/A | N/A | 267 | 297 | 208 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
35 | CZ Southwest-east corridor | PINT | 55 | 79 | 31 | 5 | 11 | -1 | 10 | 11 | 7 | -61 | 11 | -147 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 136 | 145 | 123 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
40 | Belgium-Luxembourg-Germany: long-term perspective | light PINT | 38 | 43 | 29 | 7 | 8 | 7 | 7 | 7 | 6 | -95 | -89 | -101 | N/A | 0 | 2 | 11 | N/A | N/A | N/A | 96 | 98 | 93 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
47 | Westtirol (AT) - Vöhringen (DE) | PINT | 69 | 80 | 57 | 17 | 23 | 11 | 7 | 16 | 4 | -225 | -140 | -328 | N/A | 0 | 5 | 24 | N/A | N/A | N/A | 92 | 210 | 47 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
81 | North South Interconnector | TOOT | 19 | 27 | 11 | -15 | -10 | -18 | 15 | 18 | 10 | 192 | 235 | 133 | N/A | 3 | 0 | 0 | N/A | N/A | N/A | 192 | 230 | 123 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
85 | Integration of RES in Alentejo | TOOT | 17 | 21 | 11 | 3 | 8 | 0 | 39 | 42 | 37 | -41 | 2 | -101 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 502 | 543 | 476 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
94 | GerPol Improvements | TOOT | 229 | 250 | 207 | 33 | 37 | 29 | 61 | 69 | 53 | -426 | -372 | -480 | N/A | 0 | 9 | 47 | N/A | N/A | N/A | 786 | 879 | 693 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
103 | Reinforcements Ring NL phase I | TOOT | 44 | 47 | 40 | 8 | 9 | 5 | 12 | 16 | 7 | -103 | -63 | -121 | N/A | 0 | 2 | 11 | N/A | N/A | N/A | 162 | 203 | 87 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
107 | Celtic Interconnector | TOOT | 203 | 255 | 168 | 27 | 28 | 26 | 146 | 153 | 139 | -344 | -336 | -353 | N/A | 0 | 8 | 38 | N/A | N/A | N/A | 1883 | 1933 | 1814 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
111 | Aurora line (3rd AC Finland-Sweden north) | TOOT | 85 | 95 | 74 | 7 | 10 | 6 | 76 | 77 | 76 | -94 | -79 | -122 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 1328 | 1340 | 1316 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
120 | Belgian Modular Offshore Grid II (MOG II) | TOOT | 1038 | 1054 | 1026 | 239 | 244 | 234 | 1139 | 1165 | 1112 | -3066 | -3006 | -3124 | N/A | 0 | 67 | 340 | N/A | N/A | N/A | 14677 | 14763 | 14545 | 3500 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
121 | Nautilus: multi-purpose interconnector Belgium - UK | PINT | 0 | 0 | 0 | -73 | -41 | -106 | 19 | 21 | 17 | 941 | 1356 | 527 | N/A | 17 | 0 | 0 | N/A | N/A | N/A | 249 | 267 | 230 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
123 | LitPol Link Stage 2 | TOOT | 218 | 226 | 207 | 145 | 151 | 136 | 61 | 74 | 47 | -1853 | -1742 | -1938 | N/A | 0 | 41 | 206 | N/A | N/A | N/A | 853 | 971 | 787 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
124 | NordBalt phase 2 | PINT | 54 | 64 | 46 | 14 | 16 | 12 | 29 | 37 | 24 | -184 | -148 | -207 | N/A | 0 | 4 | 20 | N/A | N/A | N/A | 403 | 481 | 320 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
126 | SE North-south short-term reinforcements | TOOT | 173 | 192 | 155 | 25 | 31 | 19 | 31 | 34 | 28 | -319 | -247 | -395 | N/A | 0 | 7 | 35 | N/A | N/A | N/A | 457 | 484 | 430 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
127 | Central Southern Italy | TOOT | 49 | 55 | 44 | 11 | 14 | 7 | 71 | 72 | 70 | -149 | -91 | -182 | N/A | 0 | 3 | 16 | N/A | N/A | N/A | 845 | 919 | 652 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
130 | HVDC SuedOstLink Wolmirstedt to area Isar | TOOT | 2174 | 2174 | 2174 | 41 | 41 | 41 | 371 | 371 | 371 | -1478 | -1478 | -1478 | 0 | 0 | 33 | 164 | 0 | 0 | 0 | 3718 | 3718 | 3718 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
132 | HVDC Line A-North | TOOT | 5249 | 5249 | 5249 | 129 | 129 | 129 | 853 | 853 | 853 | -4603 | -4603 | -4603 | 0 | 0 | 101 | 511 | 0 | 0 | 0 | 8531 | 8531 | 8531 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
138 | Black Sea Corridor | TOOT | 93 | 98 | 88 | 18 | 22 | 13 | 24 | 27 | 18 | -237 | -166 | -279 | N/A | 0 | 5 | 26 | N/A | N/A | N/A | 331 | 358 | 308 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
142 | CSE4 | TOOT | 25 | 32 | 17 | -5 | 0 | -12 | 13 | 15 | 9 | 64 | 156 | 5 | N/A | 1 | 0 | 0 | N/A | N/A | N/A | 173 | 199 | 163 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
144 | Mid Continental East corridor | TOOT | 118 | 128 | 103 | 30 | 35 | 23 | 76 | 80 | 70 | -381 | -289 | -447 | N/A | 0 | 8 | 42 | N/A | N/A | N/A | 977 | 1048 | 885 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
150 | Italy-Slovenia | light PINT | 98 | 122 | 76 | 14 | 16 | 11 | 14 | 20 | 10 | -179 | -140 | -205 | N/A | 0 | 4 | 20 | N/A | N/A | N/A | 180 | 260 | 133 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
153 | France-Alderney-Britain | PINT | 0 | 0 | 0 | -38 | -34 | -42 | 28 | 33 | 24 | 486 | 545 | 437 | N/A | 9 | 0 | 0 | N/A | N/A | N/A | 367 | 435 | 303 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
170 | Baltic States Synchronization with Continental Europe | TOOT | 301 | 325 | 283 | 205 | 217 | 195 | 89 | 91 | 88 | -2630 | -2505 | -2777 | N/A | 0 | 58 | 292 | N/A | N/A | N/A | 1150 | 1153 | 1147 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
174 | Greenconnector | PINT | 73 | 90 | 60 | 15 | 23 | 7 | 9 | 10 | 7 | -198 | -105 | -300 | N/A | 0 | 4 | 22 | N/A | N/A | N/A | 110 | 127 | 89 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
176 | Hansa PowerBridge I | TOOT | 341 | 348 | 334 | 130 | 133 | 127 | 62 | 67 | 58 | -1671 | -1631 | -1711 | N/A | 0 | 37 | 185 | N/A | N/A | N/A | 922 | 994 | 849 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
183 | DKW-DE, Westcoast | TOOT | 271 | 291 | 247 | 111 | 127 | 88 | 149 | 186 | 115 | -1426 | -1129 | -1625 | N/A | 0 | 31 | 158 | N/A | N/A | N/A | 1920 | 1975 | 1865 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
186 | East of Austria | TOOT | 417 | 417 | 416 | 122 | 134 | 111 | 451 | 460 | 441 | -1633 | -1427 | -1908 | N/A | 0 | 34 | 174 | N/A | N/A | N/A | 5841 | 5909 | 5768 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
187 | St. Peter (AT) - Pleinting (DE) | PINT | 145 | 156 | 133 | 40 | 48 | 34 | 9 | 13 | 7 | -484 | -432 | -586 | N/A | 0 | 11 | 57 | N/A | N/A | N/A | 126 | 167 | 92 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
190 | NorthConnect | TOOT | 0 | 0 | 0 | 49 | 66 | 19 | 38 | 40 | 36 | -633 | -248 | -843 | N/A | 0 | 14 | 70 | N/A | N/A | N/A | 574 | 687 | 462 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
200 | CZ Northwest-South corridor | TOOT | 63 | 69 | 54 | 7 | 12 | 2 | 10 | 13 | 7 | -92 | -19 | -160 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 140 | 173 | 121 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
210 | Würmlach (AT) - Somplago (IT) interconnection | TOOT | 16 | 26 | 6 | 4 | 7 | 1 | 2 | 4 | 1 | -55 | -10 | -93 | N/A | 0 | 1 | 6 | N/A | N/A | N/A | 27 | 48 | 13 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
219 | EuroAsia Interconnector | TOOT | 674 | 687 | 661 | 15 | 26 | 4 | 419 | 428 | 410 | -191 | -55 | -328 | N/A | 0 | 4 | 21 | N/A | N/A | N/A | 5389 | 5585 | 5192 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
225 | 2nd interconnector Belgium - Germany | light PINT | 89 | 90 | 88 | 8 | 15 | 0 | 16 | 19 | 10 | -108 | 3 | -189 | N/A | 0 | 2 | 12 | N/A | N/A | N/A | 223 | 248 | 180 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
227 | Transbalkan Corridor | TOOT | 3 | 8 | 1 | 25 | 29 | 18 | 10 | 13 | 8 | -315 | -230 | -373 | N/A | 0 | 7 | 35 | N/A | N/A | N/A | 197 | 363 | 106 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
228 | Muhlbach - Eichstetten | TOOT | 69 | 71 | 67 | 21 | 27 | 16 | 5 | 7 | 4 | -271 | -201 | -349 | N/A | 0 | 6 | 30 | N/A | N/A | N/A | 79 | 94 | 53 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
230 | GerPol Power Bridge I | TOOT | 313 | 315 | 311 | 205 | 209 | 200 | 31 | 35 | 25 | -2632 | -2562 | -2683 | N/A | 0 | 58 | 292 | N/A | N/A | N/A | 434 | 445 | 427 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
231 | Beznau - Tiengen | PINT | 12 | 18 | 10 | 14 | 20 | 6 | 9 | 11 | 6 | -185 | -73 | -258 | N/A | 0 | 4 | 21 | N/A | N/A | N/A | 122 | 138 | 98 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
235 | HVDC SuedLink Brunsbüttel/Wilster to Großgartach/Bergrheinfeld West | TOOT | 9783 | 9783 | 9783 | 248 | 248 | 248 | 1668 | 1668 | 1668 | -8869 | -8869 | -8869 | 0 | 0 | 195 | 984 | 0 | 0 | 0 | 16684 | 16684 | 16684 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
239 | Fenno-Skan 1 renewal | light PINT | 35 | 37 | 33 | 4 | 8 | 2 | 41 | 51 | 30 | -56 | -31 | -96 | N/A | 0 | 1 | 6 | N/A | N/A | N/A | 571 | 670 | 514 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
243 | New 400 kV interconnection line between Serbia and Croatia | light PINT | 10 | 18 | 5 | 1 | 3 | -2 | 3 | 4 | 2 | -15 | 25 | -35 | N/A | 0 | 0 | 2 | N/A | N/A | N/A | 34 | 58 | 20 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
244 | Vigy - Uchtelfangen area | PINT | 357 | 363 | 352 | 90 | 102 | 78 | 31 | 38 | 24 | -1153 | -1000 | -1309 | N/A | 0 | 25 | 128 | N/A | N/A | N/A | 431 | 496 | 373 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
245 | Upgrade Meeden - Diele | TOOT | 23 | 26 | 19 | 5 | 6 | 4 | 5 | 5 | 4 | -65 | -48 | -82 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 59 | 65 | 53 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
247 | AQUIND Interconnector | PINT | 8 | 18 | 0 | -62 | -57 | -67 | 35 | 36 | 33 | 793 | 859 | 727 | N/A | 14 | 0 | 0 | N/A | N/A | N/A | 377 | 471 | 242 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
250 | Merchant line Castasegna (CH) - Mese (IT) | PINT | 15 | 24 | 11 | 4 | 9 | 1 | 2 | 5 | 2 | -45 | -20 | -111 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 32 | 59 | 21 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
252 | Internal Belgian Backbone Center-East: HTLS upgrade Massenhoven-VanEyck-Gramme-Courcelles-Bruegel-Mercator | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
253 | Upstream reinforcement in France to increase FR-CH capacity | PINT | 12 | 26 | 2 | 13 | 18 | 9 | 3 | 4 | 3 | -162 | -111 | -234 | N/A | 0 | 4 | 18 | N/A | N/A | N/A | 44 | 52 | 36 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
254 | HVDC Ultranet Osterath to Philippsburg | TOOT | 1683 | 1683 | 1683 | 38 | 38 | 38 | 300 | 300 | 300 | -1366 | -1366 | -1366 | 0 | 0 | 30 | 152 | 0 | 0 | 0 | 2996 | 2996 | 2996 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
259 | HU-RO | PINT | 89 | 96 | 85 | 19 | 21 | 14 | 28 | 31 | 22 | -239 | -178 | -272 | N/A | 0 | 5 | 27 | N/A | N/A | N/A | 392 | 411 | 380 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
260 | Project 260 – Multi-purpose HVDC interconnection between Great Britain and The Netherlands | PINT | 0 | 0 | 0 | -65 | -10 | -124 | 28 | 31 | 25 | 838 | 1592 | 131 | N/A | 15 | 0 | 0 | N/A | N/A | N/A | 367 | 403 | 331 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
262 | Belgium-Netherlands: Zandvliet-Rilland | TOOT | 39 | 43 | 33 | 7 | 9 | 5 | 25 | 27 | 22 | -86 | -60 | -118 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 324 | 351 | 292 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
263 | Lake Constance East | light PINT | 143 | 147 | 139 | 33 | 34 | 31 | 15 | 19 | 13 | -422 | -403 | -434 | N/A | 0 | 9 | 47 | N/A | N/A | N/A | 200 | 241 | 176 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
267 | Hansa PowerBridge II | light PINT | 306 | 309 | 303 | 121 | 121 | 120 | 55 | 62 | 49 | -1550 | -1543 | -1556 | N/A | 0 | 34 | 172 | N/A | N/A | N/A | 811 | 841 | 780 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
270 | FR-ES project -Aragón-Atlantic Pyrenees | PINT | 274 | 280 | 271 | 60 | 65 | 56 | 238 | 243 | 229 | -763 | -723 | -828 | N/A | 0 | 17 | 85 | N/A | N/A | N/A | 3078 | 3168 | 2974 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
276 | FR-ES project -Navarra-Landes | PINT | 274 | 280 | 271 | 60 | 65 | 56 | 238 | 243 | 229 | -763 | -723 | -828 | N/A | 0 | 17 | 85 | N/A | N/A | N/A | 3078 | 3168 | 2974 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
280 | FR-BE: study Lonny-Achene-Gramme | PINT | 178 | 199 | 160 | 41 | 43 | 38 | 8 | 9 | 6 | -527 | -483 | -552 | N/A | 0 | 12 | 58 | N/A | N/A | N/A | 105 | 122 | 71 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
283 | TuNur Italy | PINT | 0 | 23 | -24 | 134 | 205 | 64 | 497 | 1000 | 0 | -1736 | -816 | -2629 | N/A | 0 | 38 | 190 | N/A | N/A | N/A | 6401 | 12829 | 0 | 4900 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
285 | GridLink | PINT | 0 | 0 | 0 | -39 | -34 | -45 | 28 | 33 | 23 | 496 | 575 | 437 | N/A | 9 | 0 | 0 | N/A | N/A | N/A | 363 | 435 | 293 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
286 | Greenlink | PINT | 36 | 107 | 0 | 0 | 2 | -3 | 96 | 102 | 91 | 4 | 39 | -24 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 1253 | 1309 | 1188 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
293 | Southern Aegean Interconnector | PINT | 83 | 86 | 80 | 21 | 23 | 19 | 79 | 93 | 65 | -276 | -247 | -298 | N/A | 0 | 6 | 31 | N/A | N/A | N/A | 1113 | 1202 | 1022 | 582 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
297 | BRABO II + III | TOOT | 39 | 43 | 33 | 7 | 9 | 5 | 25 | 27 | 22 | -86 | -60 | -118 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 324 | 351 | 292 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
299 | SACOI3 | TOOT | 131 | 140 | 117 | 33 | 37 | 28 | 74 | 78 | 68 | -418 | -365 | -479 | N/A | 0 | 9 | 46 | N/A | N/A | N/A | 950 | 993 | 887 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
309 | NeuConnect | TOOT | -2 | 9 | -20 | -51 | -51 | -51 | 25 | 29 | 22 | 688 | 725 | 650 | N/A | 12 | 0 | 0 | N/A | N/A | N/A | 326 | 383 | 277 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
312 | St. Peter (AT) - Tauern (AT) | TOOT | 288 | 330 | 259 | 70 | 79 | 59 | 25 | 33 | 18 | -924 | -757 | -1112 | N/A | 0 | 20 | 99 | N/A | N/A | N/A | 322 | 426 | 237 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
313 | Isar/Altheim/Ottenhofen (DE) - St.Peter (AT) | TOOT | 283 | 330 | 259 | 75 | 79 | 64 | 24 | 33 | 18 | -990 | -816 | -1112 | N/A | 0 | 21 | 107 | N/A | N/A | N/A | 324 | 426 | 237 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
323 | Dekani (SI) - Zaule (IT) interconnection | TOOT | 3 | 9 | 1 | 1 | 5 | -4 | 2 | 6 | 0 | -7 | 45 | -58 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 23 | 79 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
324 | Redipuglia (IT) - Vrtojba (SI) interconnection | TOOT | 4 | 7 | 0 | -1 | 0 | -3 | 2 | 6 | 0 | 12 | 38 | -5 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 28 | 81 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
325 | Obersielach (AT) - Podlog (SI) | PINT | 27 | 34 | 18 | 11 | 18 | 9 | 5 | 7 | 4 | -150 | -111 | -229 | N/A | 0 | 3 | 16 | N/A | N/A | N/A | 64 | 88 | 49 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
328 | Interconnector DE-LUX | TOOT | 8 | 11 | 2 | -3 | 0 | -7 | 2 | 3 | 1 | 37 | 90 | 1 | N/A | 1 | 0 | 0 | N/A | N/A | N/A | 25 | 44 | 9 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
329 | Stevin-Izegem/Avelgem (Ventilus): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
330 | 4th 400kV CZ-SK interconnector | light PINT | 12 | 14 | 10 | 6 | 10 | 1 | 1 | 2 | 0 | -74 | -15 | -128 | N/A | 0 | 2 | 8 | N/A | N/A | N/A | 16 | 22 | 4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
333 | PST Foretaille | PINT | 92 | 95 | 89 | 67 | 79 | 57 | 14 | 17 | 12 | -856 | -732 | -1019 | N/A | 0 | 19 | 95 | N/A | N/A | N/A | 180 | 216 | 147 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
335 | Project 335 - North Sea Wind Power Hub | light PINT | 1776 | 1790 | 1762 | 1013 | 1013 | 1013 | 4418 | 4418 | 4418 | -12981 | -12981 | -12981 | N/A | 0 | 286 | 1441 | N/A | N/A | N/A | 56007 | 56073 | 55942 | 12000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
338 | Adriatic HVDC link | PINT | 129 | 131 | 127 | 29 | 35 | 23 | 64 | 87 | 40 | -387 | -299 | -450 | N/A | 0 | 8 | 41 | N/A | N/A | N/A | 817 | 1105 | 506 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
339 | Italian HVDC tri-terminal link | PINT | 90 | 124 | 50 | 23 | 26 | 20 | 94 | 95 | 93 | -304 | -263 | -367 | N/A | 0 | 6 | 32 | N/A | N/A | N/A | 1131 | 1219 | 999 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
340 | Avelgem-Courcelles (Boucle du Hainaut): new corridor | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
341 | North CSE Corridor | PINT | 38 | 42 | 36 | 8 | 12 | 5 | 27 | 30 | 25 | -108 | -60 | -177 | N/A | 0 | 2 | 12 | N/A | N/A | N/A | 351 | 388 | 322 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
342 | Central Balkan Corridor | PINT | 24 | 30 | 20 | 6 | 8 | 4 | 12 | 17 | 8 | -80 | -54 | -97 | N/A | 0 | 2 | 9 | N/A | N/A | N/A | 152 | 225 | 100 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
343 | CSE1 New | PINT | 4 | 7 | 2 | 7 | 10 | 5 | 3 | 6 | 1 | -94 | -70 | -122 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 38 | 76 | 17 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
344 | Reinforcements Ring NL phase II | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
345 | 3rd circuit Diemen-Lelystad-Ens | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
346 | ZuidWest380 NL Oost | PINT | 27 | 31 | 21 | -1 | 1 | -2 | 20 | 20 | 19 | 10 | 30 | -9 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 257 | 263 | 253 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
347 | 3rd circuit Krimpen a/d IJssel - Geertruidenberg | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
348 | NoordWest380 NL | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
349 | MaresConnect | PINT | 0 | 1 | 0 | 2 | 7 | -2 | 135 | 143 | 128 | -22 | 25 | -88 | N/A | 0 | 0 | 2 | N/A | N/A | N/A | 1747 | 1813 | 1672 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
350 | South Balkan Corridor | TOOT | 3 | 7 | 1 | 5 | 6 | 2 | 3 | 5 | 2 | -64 | -29 | -82 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 46 | 61 | 34 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
375 | Lienz (AT) - Veneto region (IT) 220 kV | PINT | 74 | 87 | 62 | 12 | 15 | 8 | 6 | 12 | 3 | -160 | -121 | -197 | N/A | 0 | 3 | 17 | N/A | N/A | N/A | 82 | 162 | 37 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
376 | Refurbishment of the 400kV Meliti(GR)-Bitola(MK) interconnector | light PINT | 0 | 2 | -1 | 0 | 2 | -4 | 2 | 3 | 0 | 6 | 55 | -19 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 20 | 38 | 1 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
377 | Upgrade BE-NL interconnector VanEyck-Maasbracht | PINT | 34 | 55 | 21 | -1 | 1 | -2 | 19 | 20 | 18 | 16 | 30 | -9 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 247 | 263 | 225 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
378 | Transformer Gatica | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
379 | Uprate Gatica lines | TOOT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1034 | HVDC corridor from Northern Germany to Western Germany | PINT | 7224 | 7224 | 7224 | 170 | 170 | 170 | 1276 | 1276 | 1276 | -6081 | -6081 | -6081 | 0 | 0 | 134 | 675 | 0 | 0 | 0 | 12756 | 12756 | 12756 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1039 | SE North-south long-term reinforcements | light PINT | 31 | 32 | 30 | 12 | 19 | 6 | 11 | 25 | 1 | -151 | -73 | -240 | N/A | 0 | 3 | 17 | N/A | N/A | N/A | 142 | 320 | 13 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1040 | LirIC | PINT | 7 | 13 | 0 | 2 | 7 | -2 | 84 | 85 | 82 | -28 | 26 | -89 | N/A | 0 | 1 | 3 | N/A | N/A | N/A | 1080 | 1105 | 1062 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1041 | GREGY Green Energy Interconnector | PINT | 282 | 330 | 228 | -152 | -3 | -326 | 70 | 88 | 50 | 2063 | 4650 | 42 | N/A | 35 | 0 | 0 | N/A | N/A | N/A | 899 | 1143 | 650 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1042 | Offshore Wind LT 1 | PINT | 56 | 64 | 50 | 7 | 17 | 3 | 127 | 152 | 99 | -91 | -42 | -216 | N/A | 0 | 2 | 10 | N/A | N/A | N/A | 1654 | 1769 | 1498 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1046 | Finnish North-South reinforcement | PINT | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 0 | 0 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1047 | Emden-Eemshaven | light PINT | 63 | 76 | 52 | 10 | 14 | 8 | 15 | 20 | 12 | -128 | -100 | -178 | N/A | 0 | 3 | 14 | N/A | N/A | N/A | 196 | 256 | 157 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048 | Greece - Africa Power Interconnector (GAP Interconnector) | PINT | 600 | 616 | 590 | -31 | 4 | -78 | 689 | 693 | 684 | 246 | 487 | -48 | N/A | 7 | 0 | 0 | N/A | N/A | N/A | 8929 | 9005 | 8890 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1049 | Cronos Energy Ltd | PINT | 0 | 0 | 0 | -47 | -41 | -52 | 15 | 17 | 12 | 597 | 667 | 527 | N/A | 11 | 0 | 0 | N/A | N/A | N/A | 194 | 230 | 158 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1050 | Tarchon Energy Ltd | PINT | 0 | 0 | 0 | -47 | -32 | -57 | 22 | 27 | 18 | 600 | 732 | 412 | N/A | 11 | 0 | 0 | N/A | N/A | N/A | 283 | 359 | 234 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1051 | Aminth Energy Ltd | PINT | 21 | 37 | 4 | -15 | -14 | -15 | 173 | 196 | 150 | 188 | 195 | 181 | N/A | 3 | 0 | 0 | N/A | N/A | N/A | 2234 | 2567 | 1901 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1052 | Lienz (AT) - Obersielach (AT) | PINT | 24 | 29 | 18 | 12 | 18 | 8 | 5 | 7 | 4 | -154 | -108 | -229 | N/A | 0 | 3 | 17 | N/A | N/A | N/A | 68 | 88 | 46 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1054 | Westtirol (AT) - Zell/Ziller (AT) | PINT | 70 | 80 | 57 | 16 | 23 | 11 | 8 | 16 | 4 | -199 | -140 | -293 | N/A | 0 | 4 | 22 | N/A | N/A | N/A | 103 | 210 | 48 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1055 | Interconnection of Crete to the Mainland System of Greece | TOOT | 394 | 397 | 390 | 71 | 84 | 54 | 342 | 353 | 333 | -917 | -695 | -1073 | N/A | 0 | 20 | 102 | N/A | N/A | N/A | 4416 | 4471 | 4352 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1058 | HVDC Interconnector DE-CH | light PINT | 43 | 53 | 28 | 32 | 36 | 26 | 14 | 15 | 13 | -414 | -335 | -460 | N/A | 0 | 9 | 46 | N/A | N/A | N/A | 182 | 196 | 168 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1059 | Southern Italy | PINT | 6 | 8 | 1 | 2 | 2 | 1 | 10 | 12 | 6 | -22 | -17 | -30 | N/A | 0 | 0 | 2 | N/A | N/A | N/A | 124 | 159 | 81 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1063 | ZuidWest380 West | PINT | 38 | 55 | 21 | -2 | -2 | -2 | 19 | 19 | 18 | 29 | 30 | 27 | N/A | 1 | 0 | 0 | N/A | N/A | N/A | 239 | 254 | 225 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1066 | Bulgaria - Turkey | light PINT | 119 | 145 | 94 | -136 | -111 | -170 | 17 | 20 | 15 | 1742 | 2174 | 1426 | N/A | 31 | 0 | 0 | N/A | N/A | N/A | 224 | 251 | 197 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1067 | New AC 400 kV interconnection line Greece - Turkey | light PINT | 60 | 71 | 52 | -57 | -44 | -71 | 23 | 24 | 22 | 730 | 905 | 562 | N/A | 13 | 0 | 0 | N/A | N/A | N/A | 360 | 497 | 274 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1068 | LaSGo Link | light PINT | 51 | 62 | 41 | 14 | 14 | 14 | 24 | 34 | 14 | -177 | -174 | -181 | N/A | 0 | 4 | 20 | N/A | N/A | N/A | 340 | 443 | 248 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1074 | Pannonian Corridor | PINT | 9 | 13 | 4 | 5 | 7 | 4 | 2 | 3 | 1 | -65 | -46 | -87 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 24 | 39 | 15 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1082 | Sea-Socket | light PINT | 90 | 91 | 90 | 22 | 24 | 17 | 149 | 152 | 147 | -278 | -223 | -314 | N/A | 0 | 6 | 31 | N/A | N/A | N/A | 1922 | 1925 | 1919 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1085 | Malta-Italy Cable Link No.2 | PINT | 13 | 13 | 13 | 3 | 4 | 2 | 1 | 1 | 1 | -42 | -21 | -57 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 13 | 15 | 11 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1086 | Estonia internal grid reinforcement to increase RES connection capability (RRF project) | PINT | 59 | 63 | 55 | 9 | 12 | 5 | 102 | 119 | 87 | -115 | -65 | -151 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 1441 | 1504 | 1325 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1088 | Off-shore Wind Park in Latvia and Estonia - ELWIND | PINT | 16 | 19 | 12 | 11 | 17 | 7 | 180 | 207 | 151 | -138 | -90 | -220 | N/A | 0 | 3 | 15 | N/A | N/A | N/A | 2528 | 2616 | 2367 | 1000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1092 | Offshore Hybrid HVDC Interconnector BEDK | PINT | 462 | 488 | 436 | 208 | 212 | 203 | 846 | 975 | 717 | -2663 | -2605 | -2720 | N/A | 0 | 59 | 296 | N/A | N/A | N/A | 12337 | 12346 | 12328 | 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1094 | Estlink 3 | light PINT | 67 | 75 | 61 | 21 | 23 | 16 | 38 | 47 | 30 | -267 | -209 | -300 | N/A | 0 | 6 | 30 | N/A | N/A | N/A | 530 | 611 | 468 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1095 | Aurora line 2 (4th AC Finland-Sweden north) | light PINT | 56 | 61 | 52 | 5 | 8 | 2 | 61 | 70 | 52 | -70 | -32 | -106 | N/A | 0 | 2 | 8 | N/A | N/A | N/A | 858 | 892 | 799 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1096 | Beznau - Mettlen | PINT | 17 | 23 | 9 | 15 | 19 | 5 | 10 | 13 | 6 | -188 | -67 | -240 | N/A | 0 | 4 | 21 | N/A | N/A | N/A | 133 | 163 | 98 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1097 | Upgrade to Konti-Skan | PINT | 163 | 181 | 138 | 40 | 49 | 28 | 48 | 51 | 43 | -513 | -364 | -629 | N/A | 0 | 11 | 57 | N/A | N/A | N/A | 614 | 658 | 558 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1098 | Offshore Wind LT 2 | PINT | 58 | 64 | 54 | 9 | 17 | 3 | 127 | 136 | 115 | -117 | -42 | -216 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 1632 | 1759 | 1498 | 700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1100 | Reinforcement of the existing CZ-DE interconnector (Hradec - Röhrsdorf) on the CZ side | PINT | 25 | 28 | 22 | 16 | 18 | 14 | 9 | 11 | 7 | -207 | -182 | -231 | N/A | 0 | 5 | 23 | N/A | N/A | N/A | 117 | 145 | 89 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1102 | Mettlen - Ulrichen | light PINT | 8 | 13 | 2 | 4 | 7 | -1 | 3 | 7 | 2 | -48 | 15 | -88 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 48 | 88 | 20 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1103 | Bickigen - Chippis | PINT | 12 | 18 | 7 | 11 | 13 | 7 | 6 | 9 | 4 | -143 | -91 | -172 | N/A | 0 | 3 | 16 | N/A | N/A | N/A | 83 | 120 | 49 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1104 | Niederstedem - Roost | PINT | 2 | 5 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | -13 | 0 | -21 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 4 | 9 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1105 | Georgia-Romania Black Sea (submarine) interconnection cable project | PINT | 132 | 140 | 124 | -27 | -14 | -38 | 41 | 42 | 39 | 341 | 489 | 175 | N/A | 6 | 0 | 0 | N/A | N/A | N/A | 448 | 547 | 298 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1106 | Bornholm Energy Island (BEI) | TOOT | 346 | 348 | 344 | 214 | 233 | 188 | 621 | 624 | 617 | -2748 | -2405 | -2981 | N/A | 0 | 60 | 305 | N/A | N/A | N/A | 8017 | 8073 | 7909 | 2000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1107 | EuroAfrica Interconnector | PINT | 74 | 76 | 73 | 25 | 45 | 6 | 36 | 42 | 30 | -317 | -78 | -578 | N/A | 0 | 7 | 35 | N/A | N/A | N/A | 462 | 537 | 389 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1109 | Basilicata - Campania reinforcements | PINT | 13 | 17 | 4 | 0 | 3 | -2 | 18 | 26 | 12 | -5 | 21 | -39 | N/A | 0 | 0 | 0 | N/A | N/A | N/A | 234 | 327 | 151 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1110 | Sicily - Calabria | PINT | 5 | 9 | 3 | 1 | 2 | 0 | 2 | 3 | 1 | -14 | 0 | -28 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 24 | 41 | 15 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1112 | GRITA 2 | PINT | 83 | 87 | 76 | 23 | 25 | 19 | 53 | 56 | 48 | -301 | -244 | -333 | N/A | 0 | 6 | 32 | N/A | N/A | N/A | 686 | 728 | 618 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1119 | Bisamberg (AT) - Wien SO (AT) - Parndorf (AT) | PINT | 474 | 474 | 474 | 137 | 137 | 137 | 531 | 531 | 531 | -1762 | -1762 | -1762 | N/A | 0 | 39 | 196 | N/A | N/A | N/A | 6886 | 6886 | 6886 | 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1120 | Wien SO (AT) – Ternitz (AT) – Hessenberg (AT) | PINT | 135 | 135 | 135 | 39 | 39 | 39 | 130 | 130 | 130 | -504 | -504 | -504 | N/A | 0 | 11 | 56 | N/A | N/A | N/A | 1687 | 1687 | 1687 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1121 | Hessenberg (AT) - Weißenbach (AT) | PINT | 116 | 116 | 116 | 32 | 32 | 32 | 95 | 95 | 95 | -412 | -412 | -412 | N/A | 0 | 9 | 46 | N/A | N/A | N/A | 1230 | 1230 | 1230 | 600 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1122 | Offshore Wind connection Centre Manche 1 | TOOT | 268 | 281 | 251 | 56 | 63 | 53 | 386 | 388 | 384 | -724 | -677 | -808 | N/A | 0 | 16 | 80 | N/A | N/A | N/A | 5075 | 5155 | 5020 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1123 | Offshore Wind Connection Centre Manche 2 | PINT | 276 | 281 | 271 | 58 | 63 | 53 | 397 | 407 | 388 | -743 | -677 | -808 | N/A | 0 | 16 | 82 | N/A | N/A | N/A | 5103 | 5155 | 5051 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1124 | Offshore Wind Connection South Britanny | TOOT | 162 | 173 | 153 | 31 | 36 | 26 | 238 | 248 | 233 | -398 | -333 | -460 | N/A | 0 | 9 | 44 | N/A | N/A | N/A | 3080 | 3147 | 3038 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1125 | Offshore Wind Connection Occitanie | TOOT | 162 | 173 | 153 | 31 | 36 | 26 | 238 | 248 | 233 | -398 | -333 | -460 | N/A | 0 | 9 | 44 | N/A | N/A | N/A | 3080 | 3147 | 3038 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1126 | Offshore Wind Connection PACA | TOOT | 162 | 173 | 153 | 31 | 36 | 26 | 238 | 248 | 233 | -398 | -333 | -460 | N/A | 0 | 9 | 44 | N/A | N/A | N/A | 3080 | 3147 | 3038 | 750 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1127 | Offshore Wind Connection South Atlantic | PINT | 271 | 281 | 264 | 52 | 58 | 43 | 391 | 403 | 382 | -669 | -554 | -747 | N/A | 0 | 15 | 74 | N/A | N/A | N/A | 5051 | 5106 | 4998 | 1250 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1129 | New RES at Minho region | TOOT | 43 | 50 | 39 | 9 | 11 | 7 | 50 | 52 | 49 | -117 | -88 | -143 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 652 | 662 | 641 | 400 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1001st | Kaunertal Extension Project | PINT | 54 | 74 | 34 | 16 | 25 | 10 | 5 | 6 | 4 | -211 | -133 | -318 | N/A | 0 | 5 | 23 | N/A | N/A | N/A | 167 | 366 | 57 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1003st | Hydro pump storage in Bulgaria - Yadenitsa | PINT | 64 | 65 | 63 | 20 | 27 | 10 | 23 | 32 | 10 | -256 | -130 | -345 | N/A | 0 | 6 | 28 | N/A | N/A | N/A | 295 | 417 | 121 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1004st | Estonian Pumped-Hydro Energy Storage (please note the name of the Project has been changed due to location change) | PINT | 9 | 13 | 4 | 4 | 7 | 1 | 21 | 26 | 19 | -48 | -7 | -92 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 275 | 336 | 241 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1006st | HPS AMFILOCHIA | PINT | 49 | 60 | 35 | 15 | 30 | 3 | 29 | 36 | 23 | -188 | -44 | -379 | N/A | 0 | 4 | 21 | N/A | N/A | N/A | 374 | 470 | 298 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1012st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES Navaleo) | TOOT | 63 | 77 | 51 | 12 | 15 | 7 | 65 | 65 | 65 | -154 | -95 | -187 | N/A | 0 | 3 | 17 | N/A | N/A | N/A | 774 | 847 | 647 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1013st | CAES Zuidwending, NL | PINT | 20 | 35 | 4 | 14 | 20 | 8 | 4 | 4 | 3 | -179 | -105 | -252 | N/A | 0 | 4 | 20 | N/A | N/A | N/A | 47 | 58 | 37 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1025st | Silvermines Hydroelectric Power Station | PINT | 20 | 27 | 14 | 2 | 3 | 0 | 15 | 16 | 15 | -26 | -6 | -40 | N/A | 0 | 1 | 3 | N/A | N/A | N/A | 200 | 206 | 192 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1026st | Hydro pumped storage Riedl | PINT | 21 | 36 | 8 | 5 | 7 | 1 | 7 | 9 | 4 | -58 | -8 | -91 | N/A | 0 | 1 | 6 | N/A | N/A | N/A | 102 | 149 | 53 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1027st | P-PHES CUA | PINT | 55 | 56 | 53 | 9 | 10 | 7 | 31 | 41 | 21 | -111 | -90 | -124 | N/A | 0 | 2 | 12 | N/A | N/A | N/A | 401 | 516 | 275 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1035st | Ptolemaida Battery Energy Storage System | PINT | 32 | 44 | 19 | 5 | 7 | 0 | 9 | 15 | 4 | -60 | -3 | -92 | N/A | 0 | 1 | 7 | N/A | N/A | N/A | 122 | 192 | 51 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1037st | ELSEA - European Large Scale Energy Accumulation | PINT | 8 | 17 | 2 | 1 | 6 | -2 | 4 | 5 | 2 | -12 | 28 | -79 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 51 | 72 | 21 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1038st | CAES Zuidwending Extension | PINT | 19 | 37 | 0 | 10 | 21 | 0 | 4 | 7 | 0 | -135 | 2 | -272 | N/A | 0 | 3 | 15 | N/A | N/A | N/A | 48 | 91 | 5 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1039st | Reversible Hydraulic Power Plant Los Guajares | TOOT | 18 | 36 | 0 | 6 | 11 | -3 | 16 | 29 | 0 | -74 | 41 | -144 | N/A | 0 | 2 | 8 | N/A | N/A | N/A | 202 | 368 | 0 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1041st | Purifying – Pumped Hydroelectric Energy Storage “Velilla del Río Carrión” (P-PHES VELILLA) | PINT | 16 | 23 | 7 | 0 | 1 | 0 | 12 | 14 | 9 | -5 | -1 | -11 | N/A | 0 | 0 | 1 | N/A | N/A | N/A | 153 | 179 | 109 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1044st | Green Hydrogen Hub CAES | PINT | 20 | 38 | 2 | 9 | 17 | 1 | 10 | 19 | 0 | -116 | -12 | -221 | N/A | 0 | 3 | 13 | N/A | N/A | N/A | 123 | 242 | 4 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1046st | Online Grid Controller “PSKW-Rio” | Light PINT | 24 | 29 | 21 | 5 | 11 | 2 | 10 | 15 | 6 | -68 | -25 | -144 | N/A | 0 | 1 | 8 | N/A | N/A | N/A | 131 | 197 | 76 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1048st | WSK PULS (PHES) | PINT | 29 | 38 | 25 | 6 | 9 | 2 | 7 | 8 | 4 | -78 | -20 | -120 | N/A | 0 | 2 | 9 | N/A | N/A | N/A | 94 | 138 | 52 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1050st | SE Integrator | PINT | 24 | 49 | 3 | 4 | 7 | -2 | 9 | 19 | 2 | -47 | 32 | -94 | N/A | 0 | 1 | 5 | N/A | N/A | N/A | 119 | 249 | 20 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1052st | Purifying -Pumped Hydroelectric Energy Storage (P-PHES BUSEIRO) | PINT | 25 | 30 | 16 | 6 | 10 | -2 | 15 | 18 | 14 | -73 | 27 | -134 | N/A | 0 | 2 | 8 | N/A | N/A | N/A | 197 | 229 | 174 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1054st | REVERSIBLE HYDROELECTRIC POWER PUMP "AGUAYO II" | PINT | 100 | 100 | 100 | 31 | 31 | 30 | 98 | 99 | 98 | -395 | -387 | -403 | N/A | 0 | 9 | 44 | N/A | N/A | N/A | 1256 | 1275 | 1236 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1055st | CAES Leer, Germany | PINT | 21 | 33 | 8 | 20 | 21 | 18 | 10 | 18 | 2 | -251 | -228 | -273 | N/A | 0 | 6 | 28 | N/A | N/A | N/A | 166 | 307 | 24 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1056st | CAES Etzel, Germany | PINT | 21 | 34 | 8 | 18 | 18 | 18 | 10 | 18 | 1 | -232 | -228 | -237 | N/A | 0 | 5 | 26 | N/A | N/A | N/A | 163 | 307 | 18 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1057st | CAES Harsefeld-Stade, Germany | PINT | 20 | 31 | 8 | 17 | 18 | 16 | 10 | 18 | 3 | -219 | -210 | -228 | N/A | 0 | 5 | 24 | N/A | N/A | N/A | 171 | 307 | 35 | 0 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A